## CF select
[11 empty] | Inlet water t., °C | 7 | Cooling / Heating | -5
[11 empty] | Outlet water t., °C | 12 | dT | 17.5
[11 empty] | Room t., °C | 27 |  | 2450
[5 empty] | Cassette fan coils CF | [8 empty] | 3000
[11 empty] | Desired capacity, W | 2500
[5 empty] | Technical Specifications | [5 empty] | Deviation + | 20%
[11 empty] | Deviation - | 2%
2-pipe system
Model |  |  | CF2-34-AC | CF2-51-AC | CF2-68-AC | CF2-85-AC | CF2-102-AC | CF2-136-AC | CF2-170-AC | CF2-204-AC | CF2-238-AC | CF2-289-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380 | 2890
|  | Med. | 255 | 383 | 510 | 638 | 765 | 1020 | 1275 | 1530 | 1785 | 2100
|  | Low | 170 | 255 | 340 | 425 | 510 | 680 | 850 | 1020 | 1190 | 1600
Total Cooling Capacity | W | High | 1799.5 | 2691.075 | 3598.15 | 4545.275 | 5452.55 | 7227.575 | 9084.75 | 10898.25 | 12571.75 | 15234
|  | Med. | 1440 | 2153 | 2879 | 3636 | 4362 | 5782 | 7268 | 8719 | 10057 | 12187
|  | Low | 1080 | 1615 | 2159 | 2727 | 3272 | 4337 | 5451 | 6539 | 7543 | 9140
Sensible Cooling Capacity | W | High | 1370.085 | 2027.93 | 2676.19 | 3333.19 | 4047.31 | 5407.725 | 6687.25 | 7963.5 | 9258.925 | 11161.425
|  | Med. | 1096 | 1622 | 2141 | 2667 | 3238 | 4326 | 5350 | 6371 | 7407 | 8929
|  | Low | 822 | 1217 | 1606 | 2000 | 2428 | 3245 | 4012 | 4778 | 5555 | 6697
Heating Capacity | W | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W |  | 36 | 50 | 60 | 74 | 93 | 130 | 147 | 183 | 221 | 330
Max Current | A |  | 0.15652 | 0.21739 | 0.26087 | 0.32174 | 0.40435 | 0.56522 | 0.63913 | 0.79565 | 0.96087 | 1.4348
Noise Level (H/M/L) | dB(A) | High | 37 | 39 | 41 | 43 | 45 | 46 | 48 | 50 | 52 | 57
|  | Med. | 30 | 33 | 36 | 34 | 36 | 41 | 41 | 43 | 47 | 53
|  | Low | 26 | 29 | 32 | 30 | 32 | 34 | 35 | 37 | 43 | 48
Water Flow | l/h |  | 320 | 500 | 610 | 780 | 940 | 1200 | 1650 | 1850 | 2150 | 2640
Water Pressure loss | kPa |  | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 50 | 50
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | B
Fan Type |  |  | Centrifugal Fan
Motor Type |  |  | AC Permanent Split Capacitor (PSC) type
Heat exchanger type |  |  | 2 - pipes
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size | mm |  | d26
Controller |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit Dimension W/D/H | mm | Unit | 580x580x250 |  |  | 705x705x290 |  |  | 832x832x290 |  |  | 960x960x290
| mm | Panel | 680x680x30 |  |  | 830x830x30 |  |  | 980x980x30 |  |  | 1140x1140x30
Packing Dimension W/D/H | mm | Unit | 675x675x270 |  |  | 800x800x310 |  |  | 925x925x310 |  |  | 1054x1054x305
| mm | Panel | 720x710x75 |  |  | 860x860x75 |  |  | 1010x1010x75 |  |  | 1170x1170x75
Unit Weight | kg | Unit | 16.4 |  |  | 21.5 |  |  | 26.7 |  |  | 37.6
| kg | Panel | 2.3 |  |  | 3.3 |  |  | 5.2 |  |  | 7.8
Gross Weight | kg | Unit | 19 |  |  | 24.3 |  |  | 30.5 |  |  | 42.2
| kg | Panel | 3.3 |  |  | 4.9 |  |  | 7.1 |  |  | 10.5
4-pipe system
Model |  |  |  |  | CF4-68-AC | CF4-85-AC | CF4-102-AC | CF4-136-AC | CF4-170-AC | CF4-204-AC | CF4-238-AC | CF4-289-AC
Air Flow |  |  | m3/h | High | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380 | 2890
|  |  |  | Med. | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 2100
|  |  |  | Low | 340 | 425 | 510 | 680 | 850 | 1020 | 1190 | 1600
Total Cooling Capacity |  |  | W | High | 2680.825 | 3291.15 | 3812.8 | 5051.425 | 6579.75 | 7348.25 | 8618.25 | 10811.75
|  |  |  | Med. | 2145 | 2633 | 3050 | 4041 | 5264 | 5879 | 6895 | 8649
|  |  |  | Low | 1608 | 1975 | 2288 | 3031 | 3948 | 4409 | 5171 | 6487
Sensible Cooling Capacity |  |  | W | High | 2038.9 | 2569.54 | 2989.34 | 3991.055 | 4918.685 | 5663.65 | 6571.75 | 8383.9
|  |  |  | Med. | 1631 | 2056 | 2391 | 3193 | 3935 | 4531 | 5257 | 6707
|  |  |  | Low | 1223 | 1542 | 1794 | 2395 | 2951 | 3398 | 3943 | 5030
Heating Capacity |  |  | W | High
Med.
Low
Power Supply |  |  |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power |  |  | W |  | 60 | 74 | 93 | 130 | 147 | 183 | 221 | 330
Max Current |  |  | A |  | 0.26087 | 0.32174 | 0.40435 | 0.56522 | 0.63913 | 0.79565 | 0.96087 | 1.4348
Noise Level (H/M/L) |  |  | dB(A) | High | 41 | 43 | 45 | 46 | 48 | 50 | 52 | 57
|  |  |  | Med. | 36 | 34 | 36 | 41 | 41 | 43 | 47 | 53
|  |  |  | Low | 32 | 30 | 32 | 34 | 35 | 37 | 43 | 48
Water Flow |  |  | l/h | Cooling | 450 | 540 | 625 | 830 | 1050 | 1400 | 1500 | 1800
|  |  | l/h | Heating | 260 | 355 | 440 | 550 | 700 | 725 | 980 | 1185
Water Pressure loss |  |  | kPa | Cooling | 11 | 17 | 22 | 24 | 27 | 30 | 35 | 40
|  |  | kPa | Heating | 1 | 1.5 | 2 | 3 | 6 | 8 | 9 | 10
Max. Working Pressure |  |  | Mpa |  | 1.6
Insulation Class |  |  |  |  | B
Fan Type |  |  |  |  | Centrifugal Fan
Motor Type |  |  |  |  | AC Permanent Split Capacitor (PSC) type
Heat exchanger type |  |  |  |  | 4 - pipes
Heat exchanger material |  |  |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | mm |  | d26
Controller |  |  |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit Dimension W/D/H |  |  | mm | Unit | 580x580x250 | 705x705x290 |  |  | 832x832x290 |  |  | 960x960x290
|  |  | mm | Panel | 680x680x30 | 830x830x30 |  |  | 980x980x30 |  |  | 1140x1140x30
Packing Dimension W/D/H |  |  | mm | Unit | 675x675x270 | 800x800x310 |  |  | 925x925x310 |  |  | 1054x1054x305
|  |  | mm | Panel | 720x710x75 | 860x860x75 |  |  | 1010x1010x75 |  |  | 1170x1170x75
Unit Weight |  |  | kg | Unit | 17 | 22.2 |  |  | 27.4 |  |  | 38.3
|  |  | kg | Panel | 2.3 | 3.4 |  |  | 5.2 |  |  | 7.8
Gross Weight |  |  | kg | Unit | 19.6 | 25 |  |  | 31.2 |  |  | 42.9
|  |  | kg | Panel | 3.4 | 4.9 |  |  | 7.2 |  |  | 10.5