## FH4-H Select (hidden)
[7 empty] | Inlet water temp., °C | 55
[7 empty] | Outlet water temp., °C | 45
[7 empty] | Room temp., °C | 20
[7 empty] | ∆T, °C | 30
Trench heaters FH4-H
| Technical data | [5 empty] | Desired output, W | 1200
[7 empty] | Error + | 20% | 1440
[7 empty] | Error - |  | 1200
Model |  |  | FH4-H 80 | FH4-H 123 | FH4-H 166 | FH4-H 209 | FH4-H 252 | FH4-H 296
Air flow | m3/h | 100% | 158 | 316 | 474 | 632 | 790 | 948
|  | 80% | 126 | 252 | 378 | 504 | 630 | 756
|  | 60% | 89 | 178 | 267 | 356 | 445 | 534
|  | 40% | 55 | 110 | 165 | 220 | 275 | 330
|  | 20% | 17.4 | 34.8 | 52.2 | 69.6 | 87 | 104.4
Heating Capacity at 45/35/20°C | Fan speed | 100% | 697.6863 | 1208.1884 | 2082.8488 | 2521.8806 | 3396.541 | 4281.4114
|  | 80% | 581.688 | 1007.3133 | 1736.5514 | 2102.5892 | 2831.8273 | 3569.5779
|  | 60% | 451.0117 | 781.0203 | 1346.435 | 1630.2424 | 2195.657 | 2767.6719
|  | 40% | 305.6575 | 529.3093 | 912.4995 | 1104.84 | 1488.0302 | 1875.6933
|  | 20% | 145.6253 | 252.1804 | 434.7448 | 526.3822 | 708.9467 | 893.6422
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max power (incl. actuator) | W |  | 16.3 | 21.1 | 25.9 | 30.7 | 35.5 | 40.3
Max current (incl. actuator) | W |  | 0.07087 | 0.091739 | 0.11261 | 0.13348 | 0.15435 | 0.17522
Sound pressure level | dB(A) | 100% | 30 | 31 | 32 | 34 | 36 | 37
|  | 80% | 24 | 25.5 | 26.5 | 27.5 | 29.5 | 30.5
|  | 60% | 19 | 20 | 21 | 21 | 23 | 24
|  | 40% | 17 | 18 | 19 | 19 | 20 | 21
|  | 20% | - | - | - | - | 18 | 19
Max water flow | l/h |  | 59.9902 | 103.8855 | 179.0928 | 216.8427 | 292.05 | 368.1351
Max pressure loss | kPa |  | 1.2713 | 1.72 | 2.4678 | 2.8417 | 3.6644 | 4.4122
Max. Working Pressure | Mpa | 2.5
Fan Type |  | Cross - flow
Motor Type |  | Brushless EC motor
Body Material |  | Stainless steel
Heat exchanger material |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  | 1/2" Female
Unit Dimension W/D/H | mm
Packing Dimension W/D/H | mm
Unit Weight | kg
Gross Weight | kg

## DF2 AC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF2
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | AC motors |  | 2 - pipes
Model |  |  | DF23-34-AC | DF23-51-AC | DF23-68-AC | DF23-85-AC | DF23-102-AC | DF23-136-AC | DF23-170-AC | DF23-204-AC | DF23-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2170 | 3120 | 4090 | 4750 | 6070 | 8210 | 9380 | 11650 | 12490
|  | Med. | 1975 | 2839 | 3722 | 4323 | 5524 | 7471 | 8536 | 10602 | 11366
|  | Low | 1584 | 2278 | 2986 | 3468 | 4431 | 5993 | 6847 | 8505 | 9118
Sensible Cooling Capacity | kW | High | 1860 | 2640 | 3470 | 4430 | 5410 | 7210 | 8280 | 10170 | 10790
|  | Med. | 1581 | 2244 | 2950 | 3766 | 4599 | 6129 | 7038 | 8645 | 9172
|  | Low | 1042 | 1478 | 1943 | 2481 | 3030 | 4038 | 4637 | 5695 | 6042
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
|  | 30Pa | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
|  | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Max Current | A | 12Pa | 0.12174 | 0.14783 | 0.23913 | 0.29565 | 0.37826 | 0.54348 | 0.66087 | 0.80435 | 0.8913
|  | 30Pa | 0.18261 | 0.23913 | 0.29565 | 0.37826 | 0.46957 | 0.61739 | 0.75652 | 0.91304 | 1.1
|  | 50Pa | 0.21304 | 0.28696 | 0.36522 | 0.43478 | 0.51304 | 0.75652 | 0.91304 | 1.087 | 1.3043
Max Noise Level | dB(A) | 12Pa | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
|  | 30Pa | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
|  | 50Pa | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
Water Flow | l/h |  | 373 | 536 | 703 | 851 | 1044 | 1412 | 1613 | 2004 | 2148
Water Resistance | kPa |  | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 2 - pipes
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680x493x240 | 880x493x240 | 980x493x240 | 1080x493x240 | 1180x493x240 | 1380x493x240 | 1480x493x240 | 1880x493x240 | 1880x493x240
Packing Dimension W/D/H | mm |  | 690x505x250 | 890x505x250 | 990x505x250 | 1090x505x250 | 1190x505x250 | 1390x505x250 | 1490x505x250 | 1890x505x250 | 1890x505x250
Unit Weight | kg |  | 11 | 11.9 | 15 | 16 | 17.4 | 22.1 | 24 | 29.2 | 30.4
Gross Weight | kg |  | 12.2 | 13.3 | 16.6 | 17.7 | 19.2 | 24.4 | 26.3 | 32.2 | 33.4

## DF4 AC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF4
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | AC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-AC | DF431-51-AC | DF431-68-AC | DF431-85-AC | DF431-102-AC | DF431-136-AC | DF431-170-AC | DF431-204-AC | DF431-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2170 | 3120 | 4090 | 4750 | 6070 | 8210 | 9380 | 11650 | 12490
|  | Med. | 1975 | 2839 | 3722 | 4323 | 5524 | 7471 | 8536 | 10602 | 11366
|  | Low | 1584 | 2278 | 2986 | 3468 | 4431 | 5993 | 6847 | 8505 | 9118
Sensible Cooling Capacity | kW | High | 1860 | 2640 | 3470 | 4430 | 5410 | 7210 | 8280 | 10170 | 10790
|  | Med. | 1581 | 2244 | 2950 | 3766 | 4599 | 6129 | 7038 | 8645 | 9172
|  | Low | 1042 | 1478 | 1943 | 2481 | 3030 | 4038 | 4637 | 5695 | 6042
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
|  | 30Pa | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
|  | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Max Current | A | 12Pa | 0.12174 | 0.14783 | 0.23913 | 0.29565 | 0.37826 | 0.54348 | 0.66087 | 0.80435 | 0.8913
|  | 30Pa | 0.18261 | 0.23913 | 0.29565 | 0.37826 | 0.46957 | 0.61739 | 0.75652 | 0.91304 | 1.1
|  | 50Pa | 0.21304 | 0.28696 | 0.36522 | 0.43478 | 0.51304 | 0.75652 | 0.91304 | 1.087 | 1.3043
Max Noise Level | dB(A) | 12Pa | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
|  | 30Pa | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
|  | 50Pa | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
Water Flow | l/h | Cooling | 347 | 498 | 654 | 791 | 971 | 1313 | 1500 | 1864 | 1998
|  | Heating | 146 | 190 | 271 | 341 | 446 | 487 | 593 | 698 | 854
Water Pressure loss | kPa | Cooling | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating | 5 | 12 | 17 | 28 | 25 | 16 | 18 | 23 | 29
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
|  |  |  | AC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-AC | DF422-51-AC | DF422-68-AC | DF422-85-AC | DF422-102-AC | DF422-136-AC | DF422-170-AC | DF422-204-AC | DF422-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 1920 | 2740 | 3680 | 4530 | 5400 | 6590 | 7600 | 9320 | 10010
|  | Med. | 1728 | 2466 | 3312 | 4077 | 4860 | 5931 | 6840 | 8388 | 9009
|  | Low | 1402 | 2000 | 2686 | 3307 | 3942 | 4811 | 5548 | 6804 | 7307
Sensible Cooling Capacity | kW | High | 1640 | 2320 | 3120 | 4230 | 4810 | 5790 | 6710 | 8130 | 8650
|  | Med. | 1378 | 1949 | 2621 | 3553 | 4040 | 4864 | 5636 | 6829 | 7266
|  | Low | 935 | 1322 | 1778 | 2411 | 2742 | 3300 | 3825 | 4634 | 4931
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Water Flow | l/h |  | 360 | 482 | 655 | 814 | 936 | 1285 | 1397 | 1768 | 1870
Water Resistance | kPa |  | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 11 | 11.9 | 15 | 16 | 17.4 | 22.1 | 24 | 29.2 | 30.4
Gross Weight | kg |  | 12.2 | 13.3 | 16.6 | 17.7 | 19.2 | 24.4 | 26.3 | 32.2 | 33.4

## DF2 EC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF2
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | EC motors |  | 2 - pipes
Model |  |  | DF23-34-EC | DF23-51-EC | DF23-68-EC | DF23-85-EC | DF23-102-EC | DF23-136-EC | DF23-170-EC | DF23-204-EC | DF23-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2170 | 3120 | 4090 | 4750 | 6070 | 8210 | 9380 | 11650 | 12490
|  | Med. | 1975 | 2839 | 3722 | 4323 | 5524 | 7471 | 8536 | 10602 | 11366
|  | Low | 1584 | 2278 | 2986 | 3468 | 4431 | 5993 | 6847 | 8505 | 9118
Sensible Cooling Capacity | kW | High | 1860 | 2640 | 3470 | 4430 | 5410 | 7210 | 8280 | 10170 | 10790
|  | Med. | 1581 | 2244 | 2950 | 3766 | 4599 | 6129 | 7038 | 8645 | 9172
|  | Low | 1042 | 1478 | 1943 | 2481 | 3030 | 4038 | 4637 | 5695 | 6042
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 21~35 | 22~37 | 20~39 | 22~41 | 24~43 | 28~44 | 28~46 | 29~48 | 30~50
|  | 30Pa | 22~38 | 23~40 | 21~42 | 23~44 | 25~45 | 29~46 | 29~48 | 30~50 | 31~52
|  | 50Pa | 23~40 | 24~42 | 22~44 | 24~45 | 26~47 | 30~48 | 30~50 | 31~52 | 32~54
Water Flow | l/h |  | 373 | 536 | 703 | 851 | 1044 | 1412 | 1613 | 2004 | 2148
Water Resistance | kPa |  | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 2 - pipes / 3 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 11.4 | 12.5 | 15.5 | 16.5 | 17.9 | 23.9 | 25.7 | 30.7 | 31.6
Gross Weight | kg |  | 12.6 | 13.8 | 17 | 18.2 | 19.7 | 26.2 | 28.1 | 33.7 | 34.6

## DF4 EC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2750
Ducted fan coils DF4
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 10%
[10 empty] | Deviation - | 2%
|  |  |  | EC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-EC | DF431-51-EC | DF431-68-EC | DF431-85-EC | DF431-102-EC | DF431-136-EC | DF431-170-EC | DF431-204-EC | DF431-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2170 | 3120 | 4090 | 4750 | 6070 | 8210 | 9380 | 11650 | 12490
|  | Med. | 1975 | 2839 | 3722 | 4323 | 5524 | 7471 | 8536 | 10602 | 11366
|  | Low | 1584 | 2278 | 2986 | 3468 | 4431 | 5993 | 6847 | 8505 | 9118
Sensible Cooling Capacity | kW | High | 1860 | 2640 | 3470 | 4430 | 5410 | 7210 | 8280 | 10170 | 10790
|  | Med. | 1581 | 2244 | 2950 | 3766 | 4599 | 6129 | 7038 | 8645 | 9172
|  | Low | 1042 | 1478 | 1943 | 2481 | 3030 | 4038 | 4637 | 5695 | 6042
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 21~35 | 22~37 | 20~39 | 22~41 | 24~43 | 28~44 | 28~46 | 29~48 | 30~50
|  | 30Pa | 22~38 | 23~40 | 21~42 | 23~44 | 25~45 | 29~46 | 29~48 | 30~50 | 31~52
|  | 50Pa | 23~40 | 24~42 | 22~44 | 24~45 | 26~47 | 30~48 | 30~50 | 31~52 | 32~54
Water Flow | l/h | Cooling | 347 | 498 | 654 | 791 | 971 | 1313 | 1500 | 1864 | 1998
|  | Heating | 146 | 190 | 271 | 341 | 446 | 487 | 593 | 698 | 854
Water Pressure loss | kPa | Cooling | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating | 5 | 12 | 17 | 28 | 25 | 16 | 18 | 23 | 29
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
|  |  |  | EC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-EC | DF422-51-EC | DF422-68-EC | DF422-85-EC | DF422-102-EC | DF422-136-EC | DF422-170-EC | DF422-204-EC | DF422-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 1920 | 2740 | 3680 | 4530 | 5400 | 6590 | 7600 | 9320 | 10010
|  | Med. | 1728 | 2466 | 3312 | 4077 | 4860 | 5931 | 6840 | 8388 | 9009
|  | Low | 1402 | 2000 | 2686 | 3307 | 3942 | 4811 | 5548 | 6804 | 7307
Sensible Cooling Capacity | kW | High | 1640 | 2320 | 3120 | 4230 | 4810 | 5790 | 6710 | 8130 | 8650
|  | Med. | 1378 | 1949 | 2621 | 3553 | 4040 | 4864 | 5636 | 6829 | 7266
|  | Low | 935 | 1322 | 1778 | 2411 | 2742 | 3300 | 3825 | 4634 | 4931
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Water Flow | l/h |  | 360 | 482 | 655 | 814 | 936 | 1285 | 1397 | 1768 | 1870
Water Resistance | kPa |  | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8