## FCH Select
[10 empty] | Inlet water temp., °C |  | 7
[10 empty] | Outlet water temp., °C |  | 12
[10 empty] | Room temp., °C |  | 27 | 1800
[10 empty] | ∆T, °C |  | 17.5 | 1500
| Trench fan coils FCH2 | [10 empty] | #REF!
| Technical data | [8 empty] | Desired output, W |  | 1500
[10 empty] | Error + |  | 20%
[10 empty] | Error - |  | 0%
Model |  | Fan speed | FCH2 120 | FCH2 170 | FCH2 200 | FCH2 250 | FCH2 300 | FCH4 120 | FCH4 170 | FCH4 200 | FCH4 250 | FCH4 300
Air flow | m3/h | 100% | 383 | 520 | 766 | 903 | 1040 | 383 | 520 | 766 | 903 | 1040
|  | 80% | 306.4 | 416 | 612.8 | 722.4 | 832 | 306.4 | 416 | 612.8 | 722.4 | 832
|  | 60% | 229.8 | 312 | 459.6 | 541.8 | 624 | 229.8 | 312 | 459.6 | 541.8 | 624
|  | 40% | 153.2 | 208 | 306.4 | 361.2 | 416 | 153.2 | 208 | 306.4 | 361.2 | 416
|  | 20% | 76.6 | 104 | 153.2 | 180.6 | 208 | 76.6 | 104 | 153.2 | 180.6 | 208
Sensible Cooling Capacity | W | 100% | 1013.5432 | 1824.3778 | 2027.0865 | 2837.9211 | 3648.7557 | 959.8729 | 1727.7713 | 1919.7458 | 2687.6442 | 3455.5425
|  | 80% | 837.1065 | 1506.7917 | 1674.213 | 2343.8982 | 3013.5834 | 807.9774 | 1454.3593 | 1615.9548 | 2262.3367 | 2908.7186
|  | 60% | 654.1777 | 1177.5198 | 1308.3553 | 1831.6975 | 2355.0396 | 647.0629 | 1164.7132 | 1294.1258 | 1811.7761 | 2329.4265
|  | 40% | 462.134 | 831.8412 | 924.268 | 1293.9751 | 1663.6823 | 473.1557 | 851.6802 | 946.3114 | 1324.8359 | 1703.3604
|  | 20% | 255.1262 | 459.2272 | 510.2524 | 714.3534 | 918.4544 | 277.0824 | 498.7483 | 554.1647 | 775.8306 | 997.4965
Heating Capacity | W | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 60% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power supply |  |  | 220~230V / 1Ph / 50Hz
Max power (incl. actuator) | W |  | 15 | 18 | 30 | 33 | 36 | 15 | 18 | 30 | 33 | 36
Max current (incl. actuator) | W |  | 0.63 | 0.75 | 1.25 | 1.38 | 1.5 | 0.63 | 0.75 | 1.25 | 1.38 | 1.5
Sound pressure level | dB(A) | 100% | 41 | 42 | 44 | 43 | 43 | 41 | 42 | 44 | 43 | 43
|  | 80% | 36 | 41 | 39 | 40 | 42 | 36 | 41 | 39 | 40 | 42
|  | 60% | 28 | 34 | 31 | 33 | 33 | 28 | 34 | 31 | 33 | 33
|  | 40% | 23 | 29 | 24 | 26 | 27 | 23 | 29 | 24 | 26 | 27
|  | 20% | 20 | 25 | 22 | 24 | 24 | 20 | 25 | 22 | 24 | 24
Max water flow | l/h | Cooling | 294 | 529 | 588 | 823 | 1058 | 147 | 265 | 295 | 413 | 531
| l/h | Heating | 343.98 | 618.93 | 687.96 | 962.91 | 1237.86 | 173 | 312 | 346 | 485 | 623
Max pressure loss | kPa | Cooling | 4.0564 | 24.3546 | 33.5864 | 93.2721 | 199.6574 | 0.73814 | 3.9163 | 5.2641 | 13.3963 | 27.0236
| kPa | Heating | 1.6 | 8.9 | 11.4 | 28 | 56.2 | 2.0404 | 10.8995 | 14.6202 | 37.9544 | 77.5001
Max. Working Pressure | Mpa |  | 2.5
Fan Type |  |  | Cross - flow
Motor Type |  |  | Brushless EC motor
Body Material |  |  | Stainless steel
Heat exchanger type |  |  | 2 - pipe |  |  |  |  | 4 - pipe
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 1/2" Female
Unit Dimension L/W/H | mm |  | 1200x320x130 | 1700x320x130 | 2000x320x130 | 2500x320x130 | 3000x320x130 | 1200x320x130 | 1700x320x130 | 2000x320x130 | 2500x320x130 | 3000x320x130
Packing Dimension L/W/H | mm
Unit Weight | kg |  | 21.2 | 28.9 | 33.9 | 42.2 | 51.5 | 21.2 | 28.9 | 33.9 | 42.2 | 51.5
Gross Weight | kg