## HWF Select
[7 empty] | Inlet water t., °C | 7 | Cooling / Heating | -5
[7 empty] | Outlet water t., °C | 12 | dT | 17.5
[7 empty] | Room t., °C | 27 |  | 2450
2875
|  | High wall-mounted fan coil units HWF |  |  |  |  | Desired capacity, W | 2500
[7 empty] | Deviation + | 15%
|  |  | Technical Specifications |  |  |  | Deviation - | 2%
Model |  |  | HWF43-EC | HWF51-EC | HWF68-EC | HWF85-EC | HWF102-EC | HWF120-EC
Air volume | m3/h | High | 430 | 510 | 680 | 850 | 1020 | 1200
|  | Med. | 330 | 395 | 530 | 650 | 765 | 880
|  | Low | 220 | 270 | 355 | 460 | 520 | 620
Total Cooling Capacity | W | High | 2949.75 | 3414.575 | 4051.2 | 4855.95 | 6557.1 | 7380
| W | Med. | 2360 | 2732 | 3241 | 3885 | 5246 | 5904
| W | Low | 1711 | 1980 | 2350 | 2816 | 3803 | 4280
Sensible Cooling Capacity | W | High | 2086.7772 | 2429.156 | 2981.895 | 3593.92 | 4695.785 | 5330.125
| W | Med. | 1669 | 1943 | 2386 | 2875 | 3757 | 4264
| W | Low | 1210 | 1409 | 1729 | 2084 | 2724 | 3091
Heating Capacity at 60/55°C/21°C | W | High
| W | Med.
| W | Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W |  | 13 | 19 | 25 | 37 | 42 | 57
Max Current | A |  | 0.056522 | 0.082609 | 0.1087 | 0.16087 | 0.18261 | 0.24783
Max Noise Level | dB(A) | High | 32 | 35 | 41 | 47 | 45 | 49
|  | Med. | 26 | 29 | 35 | 40 | 40 | 43
|  | Low | 18 | 22 | 25 | 30 | 31 | 34
Water Flow | m3/h
Water Pressure loss | kPa |  | 24 | 30 | 24 | 30 | 32 | 40
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Cross - flow
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 2-row finned-tube
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 1/2" Female
Drain Pan Pipe Size | mm |  | d16
Controller |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit Dimension W/D/H | mm |  | 850×291×203 | 850×291×203 | 972×302×224 | 972×302×224 | 1081×327×248 | 1081×327×248
Packing Dimension W/D/H | mm |  | 927×365×287 |  | 1044×374×304 |  | 1155×410×342
Unit Weight | kg |  | 9.8 | 9.8 | 12.7 | 12.7 | 15 | 15
Gross Weight | kg |  | 11.6 | 11.6 | 14.7 | 14.7 | 17.8 | 17.8