## FH4-H Select (hidden)
[7 empty] | Inlet water temp., °C | 55
[7 empty] | Outlet water temp., °C | 45
[7 empty] | Room temp., °C | 20
[7 empty] | ∆T, °C | 30
Trench heaters FH4-H
| Technical data | [5 empty] | Desired output, W | 1200
[7 empty] | Error + | 20% | 1440
[7 empty] | Error - |  | 1200
Model |  |  | FH4-H 80 | FH4-H 123 | FH4-H 166 | FH4-H 209 | FH4-H 252 | FH4-H 296
Air flow | m3/h | 100% | 158 | 316 | 474 | 632 | 790 | 948
|  | 80% | 126 | 252 | 378 | 504 | 630 | 756
|  | 60% | 89 | 178 | 267 | 356 | 445 | 534
|  | 40% | 55 | 110 | 165 | 220 | 275 | 330
|  | 20% | 17.4 | 34.8 | 52.2 | 69.6 | 87 | 104.4
Heating Capacity at 45/35/20°C | Fan speed | 100% | 697.6863 | 1208.1884 | 2082.8488 | 2521.8806 | 3396.541 | 4281.4114
|  | 80% | 581.688 | 1007.3133 | 1736.5514 | 2102.5892 | 2831.8273 | 3569.5779
|  | 60% | 451.0117 | 781.0203 | 1346.435 | 1630.2424 | 2195.657 | 2767.6719
|  | 40% | 305.6575 | 529.3093 | 912.4995 | 1104.84 | 1488.0302 | 1875.6933
|  | 20% | 145.6253 | 252.1804 | 434.7448 | 526.3822 | 708.9467 | 893.6422
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max power (incl. actuator) | W |  | 16.3 | 21.1 | 25.9 | 30.7 | 35.5 | 40.3
Max current (incl. actuator) | W |  | 0.07087 | 0.091739 | 0.11261 | 0.13348 | 0.15435 | 0.17522
Sound pressure level | dB(A) | 100% | 30 | 31 | 32 | 34 | 36 | 37
|  | 80% | 24 | 25.5 | 26.5 | 27.5 | 29.5 | 30.5
|  | 60% | 19 | 20 | 21 | 21 | 23 | 24
|  | 40% | 17 | 18 | 19 | 19 | 20 | 21
|  | 20% | - | - | - | - | 18 | 19
Max water flow | l/h |  | 59.9902 | 103.8855 | 179.0928 | 216.8427 | 292.05 | 368.1351
Max pressure loss | kPa |  | 1.2713 | 1.72 | 2.4678 | 2.8417 | 3.6644 | 4.4122
Max. Working Pressure | Mpa | 2.5
Fan Type |  | Cross - flow
Motor Type |  | Brushless EC motor
Body Material |  | Stainless steel
Heat exchanger material |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  | 1/2" Female
Unit Dimension W/D/H | mm
Packing Dimension W/D/H | mm
Unit Weight | kg
Gross Weight | kg

## DF2 AC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF2
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | AC motors |  | 2 - pipes
Model |  |  | DF23-34-AC | DF23-51-AC | DF23-68-AC | DF23-85-AC | DF23-102-AC | DF23-136-AC | DF23-170-AC | DF23-204-AC | DF23-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2181.4 | 3133.775 | 4109.775 | 4800.15 | 6132.3 | 8165.575 | 9399.55 | 11587.25 | 12585.5
|  | Med. | 1876 | 2695 | 3534 | 4128 | 5274 | 7022 | 8084 | 9965 | 10824
|  | Low | 1374 | 1974 | 2589 | 3024 | 3863 | 5144 | 5922 | 7300 | 7929
Sensible Cooling Capacity | kW | High | 1580.615 | 2256.665 | 2935.195 | 3416.315 | 4378.14 | 5806.785 | 6721.475 | 8238.65 | 8948.375
|  | Med. | 1359 | 1941 | 2524 | 2938 | 3765 | 4994 | 5780 | 7085 | 7696
|  | Low | 996 | 1422 | 1849 | 2152 | 2758 | 3658 | 4235 | 5190 | 5637
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
|  | 30Pa | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
|  | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Max Current | A | 12Pa | 0.12174 | 0.14783 | 0.23913 | 0.29565 | 0.37826 | 0.54348 | 0.66087 | 0.80435 | 0.8913
|  | 30Pa | 0.18261 | 0.23913 | 0.29565 | 0.37826 | 0.46957 | 0.61739 | 0.75652 | 0.91304 | 1.1
|  | 50Pa | 0.21304 | 0.28696 | 0.36522 | 0.43478 | 0.51304 | 0.75652 | 0.91304 | 1.087 | 1.3043
Max Noise Level | dB(A) | 12Pa | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
|  | 30Pa | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
|  | 50Pa | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
Max Water Flow | l/h |  | 375.1333 | 538.9123 | 706.7541 | 825.4772 | 1054.5658 | 1404.2261 | 1616.4316 | 1992.6483 | 2164.3164
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 7.06 | 13.23 | 22.44 | 27.7 | 26.61 | 46.95 | 23.23 | 32.9 | 39.08
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 2 - pipes
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680x493x240 | 880x493x240 | 980x493x240 | 1080x493x240 | 1180x493x240 | 1380x493x240 | 1480x493x240 | 1880x493x240 | 1880x493x240
Packing Dimension W/D/H | mm |  | 690x505x250 | 890x505x250 | 990x505x250 | 1090x505x250 | 1190x505x250 | 1390x505x250 | 1490x505x250 | 1890x505x250 | 1890x505x250
Unit Weight | kg |  | 11 | 11.9 | 15 | 16 | 17.4 | 22.1 | 24 | 29.2 | 30.4
Gross Weight | kg |  | 12.2 | 13.3 | 16.6 | 17.7 | 19.2 | 24.4 | 26.3 | 32.2 | 33.4

## DF4 AC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF4
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | AC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-AC | DF431-51-AC | DF431-68-AC | DF431-85-AC | DF431-102-AC | DF431-136-AC | DF431-170-AC | DF431-204-AC | DF431-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2192.4 | 3131.625 | 4127.875 | 4752.2 | 6141.7 | 8180.5 | 9335.5 | 11639.5 | 12503.25
|  | Med. | 1885 | 2693 | 3550 | 4087 | 5282 | 7035 | 8029 | 10010 | 10753
|  | Low | 1381 | 1973 | 2601 | 2994 | 3869 | 5154 | 5881 | 7333 | 7877
Sensible Cooling Capacity | kW | High | 1616.78 | 2314.105 | 3038.05 | 3499.88 | 4570.885 | 6031.75 | 6913.925 | 8286.275 | 9205.25
|  | Med. | 1390 | 1990 | 2613 | 3010 | 3931 | 5187 | 5946 | 7126 | 7917
|  | Low | 1019 | 1458 | 1914 | 2205 | 2880 | 3800 | 4356 | 5220 | 5799
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
|  | 30Pa | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
|  | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Max Current | A | 12Pa | 0.12174 | 0.14783 | 0.23913 | 0.29565 | 0.37826 | 0.54348 | 0.66087 | 0.80435 | 0.8913
|  | 30Pa | 0.18261 | 0.23913 | 0.29565 | 0.37826 | 0.46957 | 0.61739 | 0.75652 | 0.91304 | 1.1
|  | 50Pa | 0.21304 | 0.28696 | 0.36522 | 0.43478 | 0.51304 | 0.75652 | 0.91304 | 1.087 | 1.3043
Max Noise Level | dB(A) | 12Pa | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
|  | 30Pa | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
|  | 50Pa | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
Max Water Flow | l/h | Cooling | 377 | 539 | 710 | 817 | 1056 | 1407 | 1605 | 2002 | 2150
Heating
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 0.77 | 1.45 | 2.54 | 4.72 | 1.56 | 1.98 | 3.38 | 28.97 | 13.51
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
|  |  |  | AC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-AC | DF422-51-AC | DF422-68-AC | DF422-85-AC | DF422-102-AC | DF422-136-AC | DF422-170-AC | DF422-204-AC | DF422-238-AC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 1904.45 | 2737.375 | 3655.975 | 4513.825 | 5382.775 | 6581.225 | 7577.9 | 9304.75 | 10041
|  | Med. | 1638 | 2354 | 3144 | 3882 | 4629 | 5660 | 6517 | 8002 | 8635
|  | Low | 1200 | 1725 | 2303 | 2844 | 3391 | 4146 | 4774 | 5862 | 6326
Sensible Cooling Capacity | kW | High | 1411.4525 | 2010.97 | 2712.33 | 3325.785 | 3921.265 | 4842.12 | 5658.25 | 6925.175 | 7470.775
|  | Med. | 1214 | 1729 | 2333 | 2860 | 3372 | 4164 | 4866 | 5956 | 6425
|  | Low | 889 | 1267 | 1709 | 2095 | 2470 | 3051 | 3565 | 4363 | 4707
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
|  | 30Pa | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
|  | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Max Current | A | 12Pa | 0.12174 | 0.14783 | 0.23913 | 0.29565 | 0.37826 | 0.54348 | 0.66087 | 0.80435 | 0.8913
|  | 30Pa | 0.18261 | 0.23913 | 0.29565 | 0.37826 | 0.46957 | 0.61739 | 0.75652 | 0.91304 | 1.1
|  | 50Pa | 0.21304 | 0.28696 | 0.36522 | 0.43478 | 0.51304 | 0.75652 | 0.91304 | 1.087 | 1.3043
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Max Water Flow | l/h | Cooling | 328 | 471 | 629 | 776 | 926 | 1132 | 1303 | 1600 | 1727
Heating
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 6.71 | 15.33 | 9.68 | 13.95 | 24.91 | 20.18 | 15.78 | 16.29 | 20.34
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 11 | 11.9 | 15 | 16 | 17.4 | 22.1 | 24 | 29.2 | 30.4
Gross Weight | kg |  | 12.2 | 13.3 | 16.6 | 17.7 | 19.2 | 24.4 | 26.3 | 32.2 | 33.4

## DF2 EC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2875
Ducted fan coils DF2
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 15%
[10 empty] | Deviation - | 2%
|  |  |  | EC motors |  | 2 - pipes
Model |  |  | DF23-34-EC | DF23-51-EC | DF23-68-EC | DF23-85-EC | DF23-102-EC | DF23-136-EC | DF23-170-EC | DF23-204-EC | DF23-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2181.4 | 3133.775 | 4109.775 | 4800.15 | 6132.3 | 8165.575 | 9399.55 | 11587.25 | 12585.5
|  | Med. | 1876 | 2695 | 3534 | 4128 | 5274 | 7022 | 8084 | 9965 | 10824
|  | Low | 1374 | 1974 | 2589 | 3024 | 3863 | 5144 | 5922 | 7300 | 7929
Sensible Cooling Capacity | kW | High | 1580.615 | 2256.665 | 2935.195 | 3416.315 | 4378.14 | 5806.785 | 6721.475 | 8238.65 | 8948.375
|  | Med. | 1359 | 1941 | 2524 | 2938 | 3765 | 4994 | 5780 | 7085 | 7696
|  | Low | 996 | 1422 | 1849 | 2152 | 2758 | 3658 | 4235 | 5190 | 5637
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Max Water Flow | l/h |  | 375.1333 | 538.9123 | 706.7541 | 825.4772 | 1054.5658 | 1404.2261 | 1616.4316 | 1992.6483 | 2164.3164
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 7.06 | 13.23 | 22.44 | 27.7 | 26.61 | 46.95 | 23.23 | 32.9 | 39.08
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 2 - pipes / 3 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 11.4 | 12.5 | 15.5 | 16.5 | 17.9 | 23.9 | 25.7 | 30.7 | 31.6
Gross Weight | kg |  | 12.6 | 13.8 | 17 | 18.2 | 19.7 | 26.2 | 28.1 | 33.7 | 34.6

## DF4 EC Select
[12 empty] | Cooling / Heating | -5
[10 empty] | Inlet water t., °C | 7 | dT | 17.5
[10 empty] | Outlet water t., °C | 12 |  | 2450
[10 empty] | Room t., °C | 27 |  | 2750
Ducted fan coils DF4
[10 empty] | Desired capacity, W | 2500
|  |  |  | Technical specifications | [5 empty] | Deviation + | 10%
[10 empty] | Deviation - | 2%
|  |  |  | EC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-EC | DF431-51-EC | DF431-68-EC | DF431-85-EC | DF431-102-EC | DF431-136-EC | DF431-170-EC | DF431-204-EC | DF431-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 2192.4 | 3131.625 | 4127.875 | 4752.2 | 6141.7 | 8180.5 | 9335.5 | 11639.5 | 12503.25
|  | Med. | 1885 | 2693 | 3550 | 4087 | 5282 | 7035 | 8029 | 10010 | 10753
|  | Low | 1381 | 1973 | 2601 | 2994 | 3869 | 5154 | 5881 | 7333 | 7877
Sensible Cooling Capacity | kW | High | 1616.78 | 2314.105 | 3038.05 | 3499.88 | 4570.885 | 6031.75 | 6913.925 | 8286.275 | 9205.25
|  | Med. | 1390 | 1990 | 2613 | 3010 | 3931 | 5187 | 5946 | 7126 | 7917
|  | Low | 1019 | 1458 | 1914 | 2205 | 2880 | 3800 | 4356 | 5220 | 5799
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Max Water Flow | l/h | Cooling | 377 | 539 | 710 | 817 | 1056 | 1407 | 1605 | 2002 | 2150
Heating
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 0.77 | 1.45 | 2.54 | 4.72 | 1.56 | 1.98 | 3.38 | 28.97 | 13.51
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
|  |  |  | EC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-EC | DF422-51-EC | DF422-68-EC | DF422-85-EC | DF422-102-EC | DF422-136-EC | DF422-170-EC | DF422-204-EC | DF422-238-EC
Air Flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
|  | Low | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
Total Cooling Capacity | kW | High | 1904.45 | 2737.375 | 3655.975 | 4513.825 | 5382.775 | 6581.225 | 7577.9 | 9304.75 | 10041
|  | Med. | 1638 | 2354 | 3144 | 3882 | 4629 | 5660 | 6517 | 8002 | 8635
|  | Low | 1200 | 1725 | 2303 | 2844 | 3391 | 4146 | 4774 | 5862 | 6326
Sensible Cooling Capacity | kW | High | 1411.4525 | 2010.97 | 2712.33 | 3325.785 | 3921.265 | 4842.12 | 5658.25 | 6925.175 | 7470.775
|  | Med. | 1214 | 1729 | 2333 | 2860 | 3372 | 4164 | 4866 | 5956 | 6425
|  | Low | 889 | 1267 | 1709 | 2095 | 2470 | 3051 | 3565 | 4363 | 4707
Heating Capacity | kW | High
Med.
Low
Power Supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max Power | W | 12Pa | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
|  | 30Pa | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
|  | 50Pa | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
Max Current | A | 12Pa | 0.073913 | 0.086957 | 0.15652 | 0.1913 | 0.24348 | 0.33913 | 0.38261 | 0.49565 | 0.60435
|  | 30Pa | 0.11304 | 0.14783 | 0.18261 | 0.22174 | 0.27391 | 0.39565 | 0.43913 | 0.6087 | 0.72174
|  | 50Pa | 0.12609 | 0.16522 | 0.21304 | 0.24348 | 0.34783 | 0.43913 | 0.54348 | 0.75217 | 0.90435
Max Noise Level | dB(A) | 12Pa | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
|  | 30Pa | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
|  | 50Pa | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
Max Water Flow | l/h | Cooling | 328 | 471 | 629 | 776 | 926 | 1132 | 1303 | 1600 | 1727
Heating
Max Water Pressure loss | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 6.71 | 15.33 | 9.68 | 13.95 | 24.91 | 20.18 | 15.78 | 16.29 | 20.34
Max. Working Pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Inlet/Outlet Water Pipe Size |  |  | 3/4" Female
Drain Pan Pipe Size |  |  | 3/4" Male
Unit Dimension W/D/H | mm |  | 680*493*240 | 880*493*240 | 980*493*240 | 1080*493*240 | 1180*493*240 | 1380*493*240 | 1480*493*240 | 1880*493*240 | 1880*493*240
Packing Dimension W/D/H | mm |  | 690*505*250 | 890*505*250 | 990*505*250 | 1090*505*250 | 1190*505*250 | 1390*505*250 | 1490*505*250 | 1890*505*250 | 1890*505*250
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8