## CF AC Select
[11 empty] | Inlet water t., °C | 7 | Cooling / Heating
[11 empty] | Outlet water t., °C | 12 | dT
[11 empty] | Room t., °C | 27
[5 empty] | Cassette Fan Coil Units CF | [5 empty] | Room relative humidity, % | 47
dx latent 2-pipe
[5 empty] | Technical Specifications | [5 empty] | Required capacity, W | 2500 | dx latent 4-pipe
[11 empty] | Deviation + | 20%
[5 empty] | AC motors |  | 2 - pipe |  |  |  | Deviation - | 2%
Model |  |  |  | CF2-51-AC | CF2-68-AC | CF2-85-AC | CF2-102-AC | CF2-136-AC | CF2-170-AC | CF2-204-AC | CF2-238-AC | CF2-289-AC
Air flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380 | 2890
|  | Med. | 255 | 383 | 510 | 638 | 765 | 1020 | 1275 | 1530 | 1785 | 2100
|  | Low | 170 | 255 | 340 | 425 | 510 | 680 | 850 | 1020 | 1190 | 1600
Total cooling capacity | W | High
Med.
Low
Sensible cooling capacity | W | High
Med.
Low
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  | 36 | 50 | 60 | 74 | 93 | 130 | 147 | 183 | 221 | 330
Max. running current | A |  |  | 0.21739 | 0.26087 | 0.32174 | 0.40435 | 0.56522 | 0.63913 | 0.79565 | 0.96087 | 1.4348
Max. sound pressure level | dB(A) | High | 37 | 39 | 41 | 43 | 45 | 46 | 48 | 50 | 52 | 57
|  | Med. | 30 | 33 | 36 | 34 | 36 | 41 | 41 | 43 | 47 | 53
|  | Low | 26 | 29 | 32 | 30 | 32 | 34 | 35 | 37 | 43 | 48
Water flow rate | l/h |  |  | 416.5829 | 549.8447 | 691.6981 | 836.7719 | 1108.5668 | 1386.0991 | 1650.707 | 1917.3264 | 2315.5116
Water-side pressure drop | kPa | Cooling 7/12/27C | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 50 | 50
|  | Heating 75/65/20C | 33.41 | 30.56 | 36.34 | 34.64 | 45.98 | 50.17 | 41.3 | 47.1 | 59.57 | 62.03
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | B
Fan Type |  |  | Centrifugal Fan
Motor Type |  |  | AC Permanent Split Capacitor (PSC) type
Heat exchanger type |  |  | 2 - pipes
Heat exchanger material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection | mm |  | d26
Controller |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit dimensions W × D × H | mm | Unit | 580x580x250 |  |  | 705x705x290 |  |  | 832x832x290 |  |  | 960x960x290
| mm | Panel | 680x680x30 |  |  | 830x830x30 |  |  | 980x980x30 |  |  | 1140x1140x30
Packed dimensions W × D × H | mm | Unit | 675x675x270 |  |  | 800x800x310 |  |  | 925x925x310 |  |  | 1054x1054x305
| mm | Panel | 720x710x75 |  |  | 860x860x75 |  |  | 1010x1010x75 |  |  | 1170x1170x75
Unit weight | kg | Unit | 16.5 |  |  | 21.5 |  |  | 26.7 |  |  | 37.6
| kg | Panel | 2.3 |  |  | 3.4 |  |  | 5.2 |  |  | 7.8
Gross weight | kg | Unit | 19 |  |  | 24.3 |  |  | 30.5 |  |  | 42.2
| kg | Panel | 3.3 |  |  | 4.9 |  |  | 7.1 |  |  | 10.5
[5 empty] | AC motors |  | 4 - pipe
Model | [5 empty] | CF4-85-AC | CF4-102-AC | CF4-136-AC | CF4-170-AC | CF4-204-AC | CF4-238-AC | CF4-289-AC
Air Flow |  |  | m3/h | High | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380 | 2890
|  |  |  | Med. | 520 | 640 | 790 | 1030 | 1290 | 1500 | 1800 | 2100
|  |  |  | Low | 350 | 430 | 520 | 690 | 860 | 1030 | 1200 | 1600
Total cooling capacity |  |  | W | High
Med.
Low
Sensible cooling capacity |  |  | W | High
Med.
Low
Heating capacity |  |  | W | High
Med.
Low
Power supply |  |  |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input |  |  | W |  | 62 | 76 | 96 | 132 | 152 | 189 | 220 | 330
Max. running current |  |  | A |  |  | 0.32174 | 0.40435 | 0.56522 | 0.63913 | 0.79565 | 0.96087 | 1.4348
Max. sound pressure level |  |  | dB(A) | High | 41 | 43 | 45 | 46 | 47 | 50 | 52 | 57
|  |  |  | Med. | 36 | 34 | 36 | 41 | 41 | 43 | 47 | 53
|  |  |  | Low | 32 | 30 | 32 | 34 | 35 | 37 | 43 | 48
Water flow rate |  |  | l/h | Cooling |  | 475 | 552 | 733 | 908 | 1049 | 1216 | 1552
|  |  | l/h | Heating
Water-side pressure drop |  |  | kPa | Cooling 7/12/27C | 11 | 17 | 22 | 24 | 27 | 30 | 35 | 40
|  |  | kPa | Heating 75/65/20C | 1.54 | 2.24 | 2.92 | 3.66 | 7.94 | 11.15 | 10.82 | 15.47
Max. operating pressure |  |  | Mpa |  | 1.6
Insulation Class |  |  |  |  | B
Fan Type |  |  |  |  | Centrifugal Fan
Motor Type |  |  |  |  | AC Permanent Split Capacitor (PSC) type
Heat exchanger type |  |  |  |  | 4 - pipes
Heat exchanger material |  |  |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  |  |  | 3/4" Female
Condensate drain connection |  |  | mm |  | d26
Controller |  |  |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit dimensions W × D × H |  |  | mm | Unit | 580x580x250 | 705x705x290 |  |  | 832x832x290 |  |  | 960x960x290
|  |  | mm | Panel | 680x680x30 | 830x830x30 |  |  | 980x980x30 |  |  | 1140x1140x30
Packed dimensions W × D × H |  |  | mm | Unit | 675x675x270 | 800x800x310 |  |  | 925x925x310 |  |  | 1054x1054x305
|  |  | mm | Panel | 720x710x75 | 860x860x75 |  |  | 1010x1010x75 |  |  | 1170x1170x75
Unit weight |  |  | kg | Unit | 17 | 22.2 |  |  | 27.7 |  |  | 38.3
|  |  | kg | Panel | 2.3 | 3.4 |  |  | 5.2 |  |  | 7.8
Gross weight |  |  | kg | Unit | 19.6 | 25 |  |  | 31.2 |  |  | 42.9
|  |  | kg | Panel | 3.4 | 4.9 |  |  | 7.2 |  |  | 10.5

## CF EC Select
[10 empty] | Inlet water t., °C | 7 | Cooling / Heating
[10 empty] | Outlet water t., °C | 12 | dT
[10 empty] | Room t., °C | 27
[5 empty] | Cassette Fan Coil Units CF |  |  |  |  | Room relative humidity, % | 47
dx latent 2-pipe
[5 empty] | Technical Specifications |  |  |  |  | Required capacity, W | 2500 | dx latent 4-pipe
[10 empty] | Deviation + | 20%
[5 empty] | EC motors |  | 2 - pipe |  |  | Deviation - | 2%
Model |  |  |  | CF2-51-EC | CF2-68-EC | CF2-85-EC | CF2-102-EC | CF2-136-EC | CF2-170-EC | CF2-204-EC | CF2-238-EC
Air flow | m3/h | High | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | Med. | 255 | 383 | 510 | 638 | 765 | 1020 | 1275 | 1530 | 1785
|  | Low | 170 | 255 | 340 | 425 | 510 | 680 | 850 | 1020 | 1190
Total cooling capacity | W | High
Med.
Low
Sensible cooling capacity | W | High
Med.
Low
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  | 22 | 30 | 36 | 44 | 56 | 78 | 88 | 114 | 139
Max. running current | A |  | 0.1 | 0.14 | 0.16 | 0.2 | 0.25 | 0.35 | 0.4 | 0.52 | 0.63
Max. sound pressure level | dB(A) | High | 37 | 39 | 41 | 43 | 45 | 46 | 48 | 50 | 52
|  | Med. | 30 | 33 | 36 | 34 | 36 | 41 | 41 | 43 | 47
|  | Low | 26 | 29 | 32 | 30 | 32 | 34 | 35 | 37 | 43
Water flow rate | l/h |  |  | 418.9763 | 556.8348 | 692.6556 | 824.2706 | 1104.6293 | 1386.1109 | 1672.5021 | 1941.7618
Water-side pressure drop | kPa | Cooling 7/12/27C | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 33.09 | 30.32 | 36.37 | 34.64 | 45.65 | 49.9 | 40.87 | 46.92 | 58.99
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | B
Fan Type |  |  | Centrifugal Fan
Motor Type |  |  | EC motor
Heat exchanger type |  |  | 2 - pipes
Heat exchanger material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection | mm |  | d26
Controller |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit dimensions W × D × H | mm | Unit | 580x580x250 |  |  | 705x705x290 |  |  | 832x832x290
| mm | Panel | 680x680x30 |  |  | 830x830x30 |  |  | 980x980x30
Packed dimensions W × D × H | mm | Unit | 675x675x270 |  |  | 800x800x310 |  |  | 925x925x310
| mm | Panel | 720x710x75 |  |  | 860x860x75 |  |  | 1010x1010x75
Unit weight | kg | Unit | 16.4 |  |  | 21.5 |  |  | 26.7
| kg | Panel | 2.3 |  |  | 3.3 |  |  | 5.2
Gross weight | kg | Unit | 19 |  |  | 24.3 |  |  | 30.5
| kg | Panel | 3.3 |  |  | 4.9 |  |  | 7.1
[5 empty] | EC motors |  | 4 - pipe
Model | [5 empty] | CF4-85-EC | CF4-102-EC | CF4-136-EC | CF4-170-EC | CF4-204-EC | CF4-238-EC
Air Flow |  |  | m3/h | High | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  |  |  | Med. | 520 | 640 | 790 | 1030 | 1290 | 1500 | 1800
|  |  |  | Low | 350 | 430 | 520 | 690 | 860 | 1030 | 1200
Total cooling capacity |  |  | W | High
Med.
Low
Sensible cooling capacity |  |  | W | High
Med.
Low
Heating capacity |  |  | W | High
Med.
Low
Power supply |  |  |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input |  |  | W |  | 36 | 44 | 56 | 78 | 88 | 114 | 139
Max. running current |  |  | A |  | 0.16 | 0.2 | 0.25 | 0.35 | 0.4 | 0.52 | 0.63
Max. sound pressure level |  |  | dB(A) | High | 41 | 43 | 45 | 46 | 48 | 50 | 52
|  |  |  | Med. | 36 | 34 | 36 | 41 | 41 | 43 | 47
|  |  |  | Low | 32 | 30 | 32 | 34 | 35 | 37 | 43
Water flow rate |  |  | l/h | Cooling |  | 464 | 570 | 745 | 934 | 1075 | 1285
|  |  | l/h | Heating
Water-side pressure drop |  |  | kPa | Cooling 7/12/27C | 11 | 17 | 22 | 24 | 27 | 30 | 35
|  |  | kPa | Heating 75/65/20C | 1.56 | 2.26 | 2.98 | 3.71 | 8.05 | 11.32 | 10.99
Max. operating pressure |  |  | Mpa |  | 1.6
Insulation Class |  |  |  |  | B
Fan Type |  |  |  |  | Centrifugal Fan
Motor Type |  |  |  |  | EC motor
Heat exchanger type |  |  |  |  | 4 - pipes
Heat exchanger material |  |  |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  |  |  | 3/4" Female
Condensate drain connection |  |  | mm |  | d26
Controller |  |  |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit dimensions W × D × H |  |  | mm | Unit | 580x580x250 | 705x705x290 |  |  | 832x832x290
|  |  | mm | Panel | 680x680x30 | 830x830x30 |  |  | 980x980x30
Packed dimensions W × D × H |  |  | mm | Unit | 675x675x270 | 800x800x310 |  |  | 925x925x310
|  |  | mm | Panel | 720x710x75 | 860x860x75 |  |  | 1010x1010x75
Unit weight |  |  | kg | Unit | 17 | 22.2 |  |  | 27.4
|  |  | kg | Panel | 2.3 | 3.4 |  |  | 5.2
Gross weight |  |  | kg | Unit | 19.6 | 25 |  |  | 31.2
|  |  | kg | Panel | 3.4 | 4.9 |  |  | 7.2