## Slide 1
QUALITY. RELIABILITY. INNOVATION.
MADE IN EUROPE
SC
FREESTANDING CONVECTORS
SC and SC-H
EFFICIENT SILENT HEATING
CLASSIC DESIGN
NATURAL CONVECTION
SUITABLE FOR LOW-TEMPERATURE
SYSTEMS
HEATING
ABSOLUTE SILENCE

## Slide 2
SC and SC-H convectors work on the principle of natural convection –
without fans and without noise.
Optimally designed heat exchangers create a gentle, evenly distributed heat curtain at the window, maintain a comfortable room temperature and keep the cold from entering.
SC and SC-H are an elegant, durable and economical solution for modern architecture.
02 | FREESTANDING CONVECTORS SC
NATURAL HEAT FOR MODERN ARCHITECTURE
HEATING
Natural convection
principle
NATURAL CONVECTION
Gentle, even heat throughout the whole room volume
ABSOLUTE SILENCE
Works without fans - no mechanical noise

## Slide 3
FREESTANDING CONVECTORS SC | 03
CREATED FOR CLEAN LINES
AND A COMFORTABLE ENVIRONMENT
Commercial spaces
Residential houses
Hotels
Restaurants
Offices
WHERE DOES IT FIT?
NON-INERTIAL OPERATION
Reacts quickly to temperature changes and precisely maintains the set comfort level
RAL COLOUR PALETTE
Painted in any RAL colour
10-YEAR HEAT EXCHANGER WARRANTY
Reliability and durability for everyday use
SAFE SURFACE
The casing surface temperature does not exceed 40°C
EN 442 CERTIFIED OUTPUTS
Tested in an independent accredited laboratory according to the European standard EN 442
ABSOLUTE SILENCE
Works on the principle of natural convection without fans and mechanical noise

## Slide 4
SC or SC-H?
THE RIGHT CHOICE FOR EVERY PROJECT
04 | FREESTANDING CONVECTORS SC
SC and SC-H convectors are built using the same natural convection technology, the same copper-aluminium heat exchangers and feature identical technical characteristics
The only difference is the design
SC and SC-H convectors use identical heat transfer technology.
The choice depends only on the desired aesthetics and the architectural direction of the project.
THE ONLY DIFFERENCE IS THE DESIGN.
SC
CLASSIC DESIGN
SC-H
MODERN DESIGN
Classic form
Modern form
The same heat exchangers
The same output
The same output
The same connections
The same connections
The same heat exchangers

## Slide 5
FREESTANDING CONVECTORS SC | 05
SC
CLASSIC DESIGN
SC-H
MODERN DESIGN
WHEN TO CHOOSE SC ?
Residential houses
Perfect for flats, houses
and apartments
Classic interiors
Harmoniously matches traditional and timeless architecture
Versatile projects
A reliable and functional solution for every project
WHEN TO CHOOSE SC-H ?
Premium segment
Suitable for high-class interiors and exclusive projects
Architectural projects Becomes part of the interior and emphasises its character.
Modern interiors
Created for contemporary architecture and a modern lifestyle

## Slide 6
KEY ADVANTAGES
06 | FREESTANDING CONVECTORS SC
Why choose SC / SC-H convectors?
SC and SC-H convectors are designed to deliver reliable, safe and efficient heating for many years. Quality you will feel every day.
A RELIABLE SOLUTION FOR THE LONG TERM.
NO NOISE
Quiet heat transfer - comfort without disturbance
7-YEAR WARRANTY
Reliability confirmed
by a long warranty for heat exchanger
DURABILITY
High-quality materials ensure a long service life
FAST RESPONSE
Reacts quickly to temperature changes and ensures comfort
NO ELECTRICITY
Works without electricity or electronics - reliable and durable
EN 442 CERTIFICATION
Meets the strict requirements of the European standard EN 442
NATURAL CONVECTION
Heat is distributed naturally, efficiently
and evenly
LOW SURFACE TEMPERATURE
Safe surface - no risk of burns
HIGH WORKING PRESSURE
Suitable for high pressure
systems
EASY INSTALLATION
The simple construction allows fast and easy installation

## Slide 7
FREESTANDING CONVECTORS SC | 07
CONSTRUCTION AND MATERIALS
High-quality materials.
Reliable construction.
SC
CLASSIC DESIGN
SC-H
MODERN DESIGN
1
4
2
3
5
1
Steel casing, powder-coated
2
Steel feet, powder-coated
3
Heat exchanger protection –
fixing elements
4
Copper - aluminium heat exchanger
5
Air vent
1
Steel casing, powder-coated
2
Steel feet, powder-coated
3
Steel heat exchanger holders,
powder-coated
4
Feet covers
5
6
Copper-aluminium heat exchanger
7
Air vent
1
6
2
3
4
5
7
FIXING SYSTEM
Sturdy feet and fixing elements ensure stable installation and reliable operation
POWDER COATING
Scratch- and corrosion-resistant powder coating preserves the aesthetic appearance for many years
COPPER-ALUMINIUM
HEAT EXCHANGER
High-quality copper tubes and profiled aluminium fins ensure efficient heat transfer
STEEL CASING
A sturdy steel casing, powder-coated, ensures long-lasting durability
Heat exchanger protection –
fixing elements

## Slide 8
DESIGN OPTIONS
A convector that adapts to your architecture
08 | FREESTANDING CONVECTORS SC
MODERN HOME
Clean lines, bright spaces and natural comfort
OFFICE
Discreet design, efficient heating and everyday convenience
PREMIUM INTERIOR
Exclusive materials, a luxurious feel and the highest quality
QUALITY AND
DURABILITY
High-quality powder
coating ensures durability and longevity
UNLIMITED
DESIGN OPTIONS
A wide colour palette allows a perfect match with any interior style
SUITABLE FOR ALL TYPES OF INTERIORS
For modern homes, offices, hotels and commercial spaces
STANDARD COLOUR
WHITE
RAL 9016
CUSTOM COLOURS ON REQUEST
Painting in any RAL colour is possible.
RAL 7016 Anthracite Grey
RAL 9005
Jet Black
RAL 7024 Graphite Grey
RAL 7044
Silk Grey
RAL 7006
Beige Grey
RAL 1035
Pearl Beige
RAL of choice

## Slide 9
HEIGHTS
LENGTH
60 - 290 cm (every 10 cm)
WIDTH
14 / 19 / 24 cm
HEIGHT
14,5-15,0 / 21,5 / 26,5 / 33,0 cm
Compact
14 cm
19 cm
Versatile
24 cm
Powerful
MODELS, DIMENSIONS AND OUTPUTS
SC and SC-H models are manufactured in 288 width, height and length versions, so they can be adapted to the requirements of the most varied projects
FREESTANDING CONVECTORS SC | 09
WIDTHS
Low profile
14,5 cm (SC)
15,0 cm (SC-H)
21,5 cm
Standard
33,0 cm
Maximum output
Increased output
26,5 cm
CONSTRUCTION AND CONNECTION OPTIONS
SC
Mounting:
floor
Connections:
bottom
SC-S
SC-W
SC-WS
Mounting:
floor
Connections:
end
Mounting:
wall
Connections:
bottom
Mounting:
wall
Connections:
end

## Slide 10
THERMAL OUTPUT (W) AT 65/55/20°C EN 442
Width (cm) | Height (cm) | Length (cm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290
14 | 14,5/15,0 | 130 | 163 | 196 | 229 | 261 | 294 | 327 | 360 | 393 | 426 | 459 | 492 | 525 | 557 | 590 | 623 | 656 | 689 | 722 | 755 | 788 | 821 | 854 | 886
 | 21,5 | 197 | 246 | 296 | 346 | 396 | 446 | 495 | 545 | 595 | 645 | 695 | 744 | 794 | 844 | 894 | 943 | 993 | 1043 | 1093 | 1143 | 1192 | 1242 | 1292 | 1342
 | 26,5 | 234 | 293 | 353 | 412 | 471 | 530 | 590 | 649 | 708 | 767 | 827 | 886 | 945 | 1004 | 1064 | 1123 | 1182 | 1241 | 1300 | 1360 | 1419 | 1478 | 1537 | 1597
 | 33,0 | 271 | 340 | 409 | 478 | 546 | 615 | 684 | 752 | 821 | 890 | 958 | 1027 | 1096 | 1165 | 1233 | 1302 | 1371 | 1439 | 1508 | 1577 | 1646 | 1714 | 1783 | 1852
19 | 14,5/15,0 | 195 | 244 | 294 | 343 | 392 | 442 | 491 | 540 | 590 | 639 | 688 | 738 | 787 | 836 | 886 | 935 | 984 | 1034 | 1083 | 1132 | 1182 | 1231 | 1280 | 1330
 | 21,5 | 295 | 370 | 444 | 519 | 594 | 668 | 743 | 818 | 892 | 967 | 1042 | 1116 | 1191 | 1266 | 1341 | 1415 | 1490 | 1565 | 1639 | 1714 | 1789 | 1863 | 1938 | 2013
 | 26,5 | 351 | 440 | 529 | 618 | 707 | 795 | 884 | 973 | 1062 | 1151 | 1240 | 1329 | 1418 | 1506 | 1595 | 1684 | 1773 | 1862 | 1951 | 2040 | 2128 | 2217 | 2306 | 2395
 | 33,0 | 402 | 504 | 606 | 708 | 809 | 911 | 1013 | 1115 | 1217 | 1318 | 1420 | 1522 | 1624 | 1726 | 1827 | 1929 | 2031 | 2133 | 2235 | 2336 | 2438 | 2540 | 2642 | 2744
24 | 14,5/15,0 | 274 | 344 | 413 | 483 | 552 | 622 | 691 | 761 | 830 | 899 | 969 | 1038 | 1108 | 1177 | 1247 | 1316 | 1386 | 1455 | 1525 | 1594 | 1664 | 1733 | 1802 | 1872
 | 21,5 | 410 | 514 | 618 | 722 | 826 | 930 | 1034 | 1138 | 1241 | 1345 | 1449 | 1553 | 1657 | 1761 | 1865 | 1969 | 2073 | 2176 | 2280 | 2384 | 2488 | 2592 | 2696 | 2800
 | 26,5 | 472 | 591 | 710 | 830 | 949 | 1069 | 1188 | 1307 | 1427 | 1546 | 1666 | 1785 | 1904 | 2024 | 2143 | 2263 | 2382 | 2501 | 2621 | 2740 | 2860 | 2979 | 3098 | 3218
 | 33,0 | 533 | 668 | 803 | 938 | 1072 | 1207 | 1342 | 1477 | 1612 | 1747 | 1882 | 2017 | 2152 | 2287 | 2422 | 2556 | 2691 | 2826 | 2961 | 3096 | 3231 | 3366 | 3501 | 3636
MODELS, DIMENSIONS AND OUTPUTS
10 | FREESTANDING CONVECTORS SC
THERMAL OUTPUT (W) AT 55/45/20°C EN 442
Width (cm) | Height (cm) | Length (cm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290
14 | 14,5/15,0 | 86 | 108 | 130 | 152 | 174 | 196 | 218 | 239 | 261 | 283 | 305 | 327 | 349 | 371 | 393 | 414 | 436 | 458 | 480 | 502 | 524 | 546 | 567 | 589
 | 21,5 | 129 | 162 | 195 | 227 | 260 | 293 | 325 | 358 | 391 | 423 | 456 | 489 | 522 | 554 | 587 | 620 | 652 | 685 | 718 | 750 | 783 | 816 | 849 | 881
 | 26,5 | 154 | 192 | 231 | 270 | 309 | 348 | 387 | 426 | 465 | 503 | 542 | 581 | 620 | 659 | 698 | 737 | 776 | 814 | 853 | 892 | 931 | 970 | 1009 | 1048
 | 33,0 | 178 | 223 | 268 | 313 | 358 | 403 | 448 | 493 | 538 | 583 | 628 | 673 | 718 | 764 | 809 | 854 | 899 | 944 | 989 | 1034 | 1079 | 1124 | 1169 | 1214
19 | 14,5/15,0 | 130 | 162 | 195 | 228 | 261 | 294 | 326 | 359 | 392 | 425 | 458 | 490 | 523 | 556 | 589 | 622 | 654 | 687 | 720 | 753 | 786 | 818 | 851 | 884
 | 21,5 | 194 | 243 | 292 | 341 | 390 | 439 | 488 | 537 | 586 | 635 | 684 | 733 | 782 | 831 | 881 | 930 | 979 | 1028 | 1077 | 1126 | 1175 | 1224 | 1273 | 1322
 | 26,5 | 230 | 289 | 347 | 405 | 464 | 522 | 580 | 639 | 697 | 755 | 813 | 872 | 930 | 988 | 1047 | 1105 | 1163 | 1222 | 1280 | 1338 | 1397 | 1455 | 1513 | 1572
 | 33,0 | 261 | 328 | 394 | 460 | 526 | 592 | 658 | 725 | 791 | 857 | 923 | 989 | 1056 | 1122 | 1188 | 1254 | 1320 | 1386 | 1453 | 1519 | 1585 | 1651 | 1717 | 1783
24 | 14,5/15,0 | 185 | 232 | 278 | 325 | 372 | 419 | 465 | 512 | 559 | 606 | 653 | 699 | 746 | 793 | 840 | 886 | 933 | 980 | 1027 | 1074 | 1120 | 1167 | 1214 | 1261
 | 21,5 | 268 | 336 | 404 | 472 | 540 | 608 | 676 | 744 | 812 | 880 | 947 | 1015 | 1083 | 1151 | 1219 | 1287 | 1355 | 1423 | 1491 | 1559 | 1627 | 1695 | 1762 | 1830
 | 26,5 | 307 | 384 | 462 | 539 | 617 | 695 | 772 | 850 | 927 | 1005 | 1083 | 1160 | 1238 | 1316 | 1393 | 1471 | 1548 | 1626 | 1704 | 1781 | 1859 | 1936 | 2014 | 2092
 | 33,0 | 345 | 432 | 519 | 607 | 694 | 781 | 869 | 956 | 1043 | 1131 | 1218 | 1305 | 1393 | 1480 | 1567 | 1654 | 1742 | 1829 | 1916 | 2004 | 2091 | 2178 | 2266 | 2353
THERMAL OUTPUT (W) AT 75/65/20°C EN 442
Width (cm) | Height (cm) | Length (cm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290
14 | 14,5/15,0 | 178 | 223 | 269 | 314 | 359 | 404 | 449 | 494 | 539 | 585 | 630 | 675 | 720 | 765 | 810 | 855 | 901 | 946 | 991 | 1036 | 1081 | 1126 | 1171 | 1217
 | 21,5 | 272 | 341 | 410 | 479 | 548 | 617 | 686 | 755 | 824 | 893 | 962 | 1031 | 1100 | 1169 | 1238 | 1307 | 1376 | 1445 | 1514 | 1583 | 1652 | 1721 | 1790 | 1859
 | 26,5 | 324 | 407 | 489 | 571 | 653 | 735 | 817 | 900 | 982 | 1064 | 1146 | 1228 | 1310 | 1392 | 1475 | 1557 | 1639 | 1721 | 1803 | 1885 | 1968 | 2050 | 2132 | 2214
 | 33,0 | 377 | 472 | 567 | 663 | 758 | 853 | 948 | 1044 | 1139 | 1234 | 1330 | 1425 | 1520 | 1616 | 1711 | 1806 | 1902 | 1997 | 2092 | 2188 | 2283 | 2378 | 2474 | 2569
19 | 14,5/15,0 | 267 | 335 | 403 | 471 | 538 | 606 | 674 | 741 | 809 | 877 | 945 | 1012 | 1080 | 1148 | 1215 | 1283 | 1351 | 1419 | 1486 | 1554 | 1622 | 1689 | 1757 | 1825
 | 21,5 | 409 | 512 | 616 | 719 | 823 | 926 | 1029 | 1133 | 1236 | 1340 | 1443 | 1547 | 1650 | 1754 | 1857 | 1961 | 2064 | 2168 | 2271 | 2374 | 2478 | 2581 | 2685 | 2788
 | 26,5 | 487 | 610 | 733 | 856 | 980 | 1103 | 1226 | 1349 | 1473 | 1596 | 1719 | 1842 | 1965 | 2089 | 2212 | 2335 | 2458 | 2582 | 2705 | 2828 | 2951 | 3074 | 3198 | 3321
 | 33,0 | 562 | 704 | 846 | 988 | 1130 | 1273 | 1415 | 1557 | 1699 | 1841 | 1984 | 2126 | 2268 | 2410 | 2552 | 2695 | 2837 | 2979 | 3121 | 3263 | 3406 | 3548 | 3690 | 3832
24 | 14,5/15,0 | 373 | 467 | 562 | 656 | 750 | 845 | 939 | 1034 | 1128 | 1222 | 1317 | 1411 | 1505 | 1600 | 1694 | 1789 | 1883 | 1977 | 2072 | 2166 | 2261 | 2355 | 2449 | 2544
 | 21,5 | 571 | 715 | 860 | 1004 | 1148 | 1293 | 1437 | 1582 | 1726 | 1871 | 2015 | 2160 | 2304 | 2448 | 2593 | 2737 | 2882 | 3026 | 3171 | 3315 | 3460 | 3604 | 3749 | 3893
 | 26,5 | 659 | 825 | 992 | 1159 | 1326 | 1492 | 1659 | 1826 | 1993 | 2160 | 2326 | 2493 | 2660 | 2827 | 2993 | 3160 | 3327 | 3494 | 3660 | 3827 | 3994 | 4161 | 4327 | 4494
 | 33,0 | 747 | 936 | 1125 | 1314 | 1503 | 1692 | 1881 | 2070 | 2259 | 2448 | 2637 | 2827 | 3016 | 3205 | 3394 | 3583 | 3772 | 3961 | 4150 | 4339 | 4528 | 4717 | 4906 | 5095
Thermal outputs at non-standard temperatures are given at konveka.com:
https://konveka.com/product/trench-heaters/pastatomi-konvektoriai-sc/
https://konveka.com/product/trench-heaters/pastatomi-konvektoriai-sc-h/

## Slide 11
ACCESSORIES
Correctly selected accessories ensure convenient installation,
precise temperature regulation and smooth system operation
01
THERMOSTATIC VALVE (AXIAL)
TVA15
02
RETURN FLOW LIMITER (ANGLE)
LA15
Working temperature -10°C -120°C
Thread 1/2"
Kvs - 2,0
Kvs
Pressure class - PN10
Working temperature -10°C -120°C
Thread 1/2"
Kvs – 2,0
Kvs
Pressure class - PN10
03
THERMOSTATIC HEAD
TH
Temperature range
6°C - 28°C
Connection thread M30 x 1.5mm
Frost protection
Max. temperature limiting
Casing material
ABS
ABS
FREESTANDING CONVECTORS SC | 11
Body – nickel-
plated bronze
Ni
Body – nickel-
plated bronze
Ni
Width, cm | Height, cm | Max. water flow, l/h | Pressure loss calculation formula, Pa
14 | 14,5 (SC) 15,0 (SC-H) | 122 | (L - 0,20) x (0,0074 x q² - 0,0501 x q + 0,0796)
 | 21,5 | 190 | (L - 0,20) x (0,0078 x q² + 1,3090 x q - 20,440)
 | 26,5 | 226 | (L - 0,20) x (0,0111 x q² + 2,2429 x q - 58,220)
 | 33,0 | 246 | (L - 0,20) x (0,0157 x q² + 2,6179 x q - 40,880)
19 | 14,5 (SC) 15,0 (SC-H) | 171 | (L - 0,24) x (0,0022 x q² + 0,3040 x q + 4,120)
 | 21,5 | 265 | (L - 0,20) x (0,0111 x q² + 2,2429 x q - 58,220)
 | 26,5 | 316 | (L - 0,24) x (0,0084 x q² + 0,5728 x q + 14,976)
 | 33,0 | 344 | (L - 0,20) x (0,0301 x q² + 1,8654 x q + 5,7952)
24 | 14,5 (SC) 15,0 (SC-H) | 239 | (L - 0,20) x (0,0078 x q² + 1,3090 x q - 20,440)
 | 21,5 | 371 | (L - 0,20) x (0,0157 x q² + 2,6179 x q - 40,880)
 | 26,5 | 442 | (L - 0,20) x (0,0301 x q² + 1,8654 x q + 5,7952)
 | 33,0 | 481 | (L - 0,20) x (0,0313 x q² + 5,2215 x q - 78,190)
MAXIMUM WATER FLOW AND PRESSURE LOSS

## Slide 12
12 | FREESTANDING CONVECTORS SC
REAL PROJECTS
KONVEKA convectors are chosen in prestigious buildings worldwide, where comfort, reliability and architectural aesthetics matter most
VILNIUS, LITHUANIA
ADMINISTRATIVE BUILDING
Application
Offices
Product
SC
Colour
RAL 8025
BUSINESS CENTRE
RIGA, LATVIA
Application
Business centre
Product
SC
Grilles
Painted metal
SHOPPING CENTRE „MEGA“
KAUNAS, LITHUANIA
Application
Hotel
Product
SC
Grilles
Painted metal
HOTEL "BRITANNIA"
TRONDHEIM, NORWAY
Application
Shopping centre
Product
SC-H
Grilles
Painted metal

## Slide 13
ABOUT KONVEKA
KONVEKA is a Lithuanian engineering company that has been creating top-quality convectors and fan coils for contemporary architecture for more than 20 years.
Our solutions combine efficiency, reliability and aesthetics - so that buildings are not only functional but also inspiring
For more than two decades we have been manufacturing
convectors and fan coils
20+
YEARS OF EXPERIENCE
Our products are
used worldwide
30+
COUNTRIES
Reliable solutions in residential, commercial and public buildings
1 000+
COMPLETED PROJECTS
Created and manufactured in Lithuania,
to the highest quality standards
EUROPEAN ENGINEERING
KONVEKA SOLUTIONS - FOR CONTEMPORARY ARCHITECTURE
OFFICE COMPLEX
Vilnius, Lithuania
RESIDENTIAL COMPLEX
Stockholm, Sweden
HOTEL
Copenhagen, Denmark
CULTURAL CENTRE
Oslo, Norway
FREESTANDING CONVECTORS SC | 13
OUR VALUES
We create products that naturally blend into modern architecture
ARCHITECTURE FIRST
Top-quality materials and strict quality control
RELIABILITY
Maximum thermal efficiency and low energy consumption
EFFICIENCY
Quiet operation and even heat distribution - for comfort every day
COMFORT
A wide range of custom – made products for any project
FLEXIBLE SOLUTIONS

## Slide 14
THE CULTURE OF HEAT
+370 677 06303
sales@konveka.lt
www.konveka.com