## DF2 AC Select
Cooling / Heating
[10 empty] | Inlet water temperature, °C | 7 | dT
[10 empty] | Outlet water temperature, °C | 12
[10 empty] | Room temperature, °C | 27
[5 empty] | DF ducted fan coil units |  |  |  |  | External static pressure, Pa | 12
[10 empty] | Room relative humidity, % | 47 | dx latent
[10 empty] | Required capacity, W | 2500
[5 empty] | Technical specifications |  |  |  |  | Tolerance + | 15%
[10 empty] | Tolerance - | 2%
[5 empty] | AC motors |  | 2 - pipes
Model |  |  | DF23-34-B-AC DF23-34-E-AC | DF23-51-B-AC DF23-51-E-AC | DF23-68-B-AC DF23-68-E-AC | DF23-85-B-AC DF23-85-E-AC | DF23-102-B-AC DF23-102-E-AC | DF23-136-B-AC DF23-136-E-AC | DF23-170-B-AC DF23-170-E-AC | DF23-204-B-AC DF23-204-E-AC | DF23-238-B-AC DF23-238-E-AC
Air flow | m3/h | High |  | 567 | 770 | 963 | 1155 | 1579 | 1837 | 2268 | 2541
|  | Med. |  | 416 | 565 | 706 | 847 | 1273 | 1487 | 1836 | 2020
|  | Low |  | 274 | 372 | 465 | 558 | 953 | 1115 | 1377 | 1543
Total cooling capacity | W | High
|  | Med. |  | 2021 | 4079 | 4426 | 5840 | 7774 | 8275 | 10474 | 11005
|  | Low |  | 1753 | 2450 | 2987 | 3574 | 6448 | 6622 | 8370 | 8853
Sensible cooling capacity | W | High |  | 2463.8 | 3240.1 | 3748.15 | 4844.05 | 6550.9 | 7113.65 | 8911.65 | 9363.35
|  | Med. |  | 1579 | 3156 | 3400 | 4519 | 5955 | 6409 | 8029 | 8427
|  | Low |  | 1370 | 1895 | 2294 | 2766 | 4939 | 5129 | 6416 | 6779
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
Max. running current | A |  |  | 0.15 | 0.24 | 0.3 | 0.38 | 0.54 | 0.66 | 0.8 | 0.89
Max. sound pressure level | dB(A) |  |  | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
Water flow rate | l/h |  |  | 542.1926 | 720.1634 | 839.2003 | 1076.3543 | 1470.7137 | 1579.4841 | 1999.037 | 2102.7945
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 27.03 | 26.78 | 28.09 | 36.67 | 53.42 | 53.11 | 51.48 | 49.31 | 64.03
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 2 - pipes / 3 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 11 | 11.9 | 15 | 16 | 17.4 | 22.1 | 24 | 29.2 | 30.4
Gross Weight | kg |  | 12.2 | 13.3 | 16.6 | 17.7 | 19.2 | 24.4 | 26.3 | 32.2 | 33.4
ESP data table for DF2 AC Select - used by the formulas above, do not edit
12 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 123.3 | 173.4 | 225.1 | 286.1 | 351.2 | 464.5 | 535.1 | 653.6 | 689.2
12 Pa - s0 |  |  | -297.9 | -394 | -469.5 | -577.5 | -736.8 | -918 | -1083.8 | -1267.4 | -1271.5
12 Pa - h1 |  |  | 108.2 | 154.5 | 207.2 | 232 | 299.6 | 402.4 | 453 | 548.1 | 599.7
12 Pa - h0 |  |  | -281.7 | -393.5 | -485.5 | -535.3 | -721.1 | -897.6 | -1068 | -1225 | -1323.1
12 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
12 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
12 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
12 Pa - Max noise, dB(A) |  |  | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
30 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 123.3 | 173.4 | 225.1 | 286.1 | 351.2 | 464.5 | 535.1 | 653.6 | 689.2
30 Pa - s0 |  |  | -297.9 | -394 | -469.5 | -577.5 | -736.8 | -918 | -1083.8 | -1267.4 | -1271.5
30 Pa - h1 |  |  | 108.2 | 154.5 | 207.2 | 232 | 299.6 | 402.4 | 453 | 548.1 | 599.7
30 Pa - h0 |  |  | -281.7 | -393.5 | -485.5 | -535.3 | -721.1 | -897.6 | -1068 | -1225 | -1323.1
30 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
30 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
30 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
30 Pa - Max noise, dB(A) |  |  | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
50 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 123.3 | 173.4 | 225.1 | 286.1 | 351.2 | 464.5 | 535.1 | 653.6 | 689.2
50 Pa - s0 |  |  | -297.9 | -394 | -469.5 | -577.5 | -736.8 | -918 | -1083.8 | -1267.4 | -1271.5
50 Pa - h1 |  |  | 108.2 | 154.5 | 207.2 | 232 | 299.6 | 402.4 | 453 | 548.1 | 599.7
50 Pa - h0 |  |  | -281.7 | -393.5 | -485.5 | -535.3 | -721.1 | -897.6 | -1068 | -1225 | -1323.1
50 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
50 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
50 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
50 Pa - Max noise, dB(A) |  |  | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56

## DF4 AC Select
Cooling / Heating
[10 empty] | Inlet water temperature, °C | 7 | dT
[10 empty] | Outlet water temperature, °C | 12
[10 empty] | Room temperature, °C | 27
[5 empty] | Ducted Fan Coil Units DF |  |  |  |  | External static pressure, Pa | 12
[10 empty] | Room relative humidity, % | 47 | dx latent
[10 empty] | Required capacity, W | 2500
[5 empty] | Technical specifications |  |  |  |  | Tolerance + | 15%
[10 empty] | Tolerance - | 2%
[5 empty] | AC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-B-AC DF431-34-E-AC | DF431-51-B-AC DF431-51-E-AC | DF431-68-B-AC DF431-68-E-AC | DF431-85-B-AC DF431-85-E-AC | DF431-102-B-AC DF431-102-E-AC | DF431-136-B-AC DF431-136-E-AC | DF431-170-B-AC DF431-170-E-AC | DF431-204-B-AC DF431-204-E-AC | DF431-238-B-AC DF431-238-E-AC
Air flow | m3/h | High |  | 567 | 770 | 963 | 1155 | 1579 | 1837 | 2268 | 2541
|  | Med. |  | 416 | 565 | 706 | 847 | 1273 | 1487 | 1836 | 2020
|  | Low |  | 274 | 372 | 465 | 558 | 953 | 1115 | 1377 | 1543
Total cooling capacity | W | High
|  | Med. |  | 2636 | 3590 | 4389 | 5395 | 7679 | 8202 | 10438 | 10993
|  | Low |  | 1736 | 2160 | 2953 | 3551 | 6341 | 6605 | 8378 | 8706
Sensible cooling capacity | W | High |  | 2546.5 | 3385.25 | 3865.1 | 5112.1 | 6865.9 | 7351.65 | 8986.05 | 9662
|  | Med. |  | 2149 | 2898 | 3544 | 4412 | 6227 | 6683 | 8060 | 8870
|  | Low |  | 1416 | 1743 | 2385 | 2904 | 5143 | 5381 | 6470 | 7024
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
Max. running current | A |  |  | 0.15 | 0.24 | 0.3 | 0.38 | 0.54 | 0.66 | 0.8 | 0.89
Max. sound pressure level | dB(A) |  |  | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
Water flow rate | l/h | Cooling |  | 537 | 721 | 823 | 1075 | 1456 | 1552 | 2001 | 2059
Heating
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 11.06 | 26.5 | 37.07 | 60.26 | 54.89 | 35.28 | 39.33 | 48.81 | 62.67
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
[5 empty] | AC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-B-AC DF422-34-E-AC | DF422-51-B-AC DF422-51-E-AC | DF422-68-B-AC DF422-68-E-AC | DF422-85-B-AC DF422-85-E-AC | DF422-102-B-AC DF422-102-E-AC | DF422-136-B-AC DF422-136-E-AC | DF422-170-B-AC DF422-170-E-AC | DF422-204-B-AC DF422-204-E-AC | DF422-238-B-AC DF422-238-E-AC
Air flow | m3/h | High |  | 567 | 770 | 963 | 1155 | 1579 | 1837 | 2268 | 2541
|  | Med. |  | 416 | 565 | 706 | 847 | 1273 | 1487 | 1836 | 2020
|  | Low |  | 274 | 372 | 465 | 558 | 953 | 1115 | 1377 | 1543
Total cooling capacity | W | High
|  | Med. |  | 2452 | 3381 | 4195 | 4837 | 5610 | 6641 | 8164 | 8666
|  | Low |  | 1745 | 2368 | 2969 | 3549 | 4852 | 5337 | 6566 | 6971
Sensible cooling capacity | W | High |  | 2176.05 | 2981.05 | 3642.25 | 4292.05 | 5362.35 | 5940 | 7419.5 | 7771.05
|  | Med. |  | 1976 | 2754 | 3391 | 3854 | 4520 | 5447 | 6670 | 7072
|  | Low |  | 1406 | 1929 | 2400 | 2828 | 3909 | 4378 | 5364 | 5688
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
Max. running current | A |  |  | 0.15 | 0.24 | 0.3 | 0.38 | 0.54 | 0.66 | 0.8 | 0.89
Max. sound pressure level | dB(A) |  |  | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
Water flow rate | l/h | Cooling |  | 464 | 629 | 775 | 926 | 1144 | 1245 | 1562 | 1638
Heating | bar: 39; 43; 46; 50
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 22.35 | 25.48 | 24.9 | 36.58 | 52.24 | 41.35 | 47.02 | 43.89 | 56.54
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | AC asynchronous fan motor, 4-speed
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
ESP data table for DF4 AC Select - used by the formulas above, do not edit or move
12 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 123.3 | 176.4 | 233 | 297.8 | 361.3 | 485.6 | 560.1 | 656.8 | 716.1
12 Pa - s0 |  |  | -297.8 | -447.9 | -607.3 | -781 | -912.7 | -1287.5 | -1521.7 | -1323.2 | -1741
12 Pa - h1 |  |  | 58.7 | 76.3 | 106.9 | 132.1 | 177.4 | 195.5 | 234.2 | 263.1 | 331.9
12 Pa - h0 |  |  | -295.4 | -383.5 | -485.2 | -533.9 | -841.1 | -986.5 | -1063.1 | -824 | -1355.7
12 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
12 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
12 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
12 Pa - Max noise, dB(A) |  |  | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
30 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 123.3 | 176.4 | 233 | 297.8 | 361.3 | 485.6 | 560.1 | 656.8 | 716.1
30 Pa - s0 |  |  | -297.8 | -447.9 | -607.3 | -781 | -912.7 | -1287.5 | -1521.7 | -1323.2 | -1741
30 Pa - h1 |  |  | 58.7 | 76.3 | 106.9 | 132.1 | 177.4 | 195.5 | 234.2 | 263.1 | 331.9
30 Pa - h0 |  |  | -295.4 | -383.5 | -485.2 | -533.9 | -841.1 | -986.5 | -1063.1 | -824 | -1355.7
30 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
30 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
30 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
30 Pa - Max noise, dB(A) |  |  | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
50 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 123.3 | 176.4 | 233 | 297.8 | 361.3 | 485.6 | 560.1 | 656.8 | 716.1
50 Pa - s0 |  |  | -297.8 | -447.9 | -607.3 | -781 | -912.7 | -1287.5 | -1521.7 | -1323.2 | -1741
50 Pa - h1 |  |  | 58.7 | 76.3 | 106.9 | 132.1 | 177.4 | 195.5 | 234.2 | 263.1 | 331.9
50 Pa - h0 |  |  | -295.4 | -383.5 | -485.2 | -533.9 | -841.1 | -986.5 | -1063.1 | -824 | -1355.7
50 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
50 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
50 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
50 Pa - Max noise, dB(A) |  |  | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
ESP data table for DF4 AC Select - used by the formulas above, do not edit or move
12 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 110.6 | 154.9 | 210.9 | 282.3 | 317 | 383.9 | 452.8 | 545.9 | 578.3
12 Pa - s0 |  |  | -295.2 | -391 | -570.6 | -710.8 | -738.2 | -927.4 | -1213.2 | -1423.4 | -1469.5
12 Pa - h1 |  |  | 94.4 | 135.6 | 182.5 | 223.9 | 266.3 | 322.4 | 377.9 | 460 | 494.8
12 Pa - h0 |  |  | -266.4 | -367 | -520.4 | -625.4 | -689.1 | -896.7 | -1120.7 | -1350.3 | -1453.7
12 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
12 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
12 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 28 | 34 | 55 | 68 | 87 | 125 | 152 | 185 | 205
12 Pa - Max noise, dB(A) |  |  | 34 | 35 | 38 | 42 | 43 | 44 | 46 | 48 | 49
30 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 110.6 | 154.9 | 210.9 | 282.3 | 317 | 383.9 | 452.8 | 545.9 | 578.3
30 Pa - s0 |  |  | -295.2 | -391 | -570.6 | -710.8 | -738.2 | -927.4 | -1213.2 | -1423.4 | -1469.5
30 Pa - h1 |  |  | 94.4 | 135.6 | 182.5 | 223.9 | 266.3 | 322.4 | 377.9 | 460 | 494.8
30 Pa - h0 |  |  | -266.4 | -367 | -520.4 | -625.4 | -689.1 | -896.7 | -1120.7 | -1350.3 | -1453.7
30 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
30 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
30 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 42 | 55 | 68 | 87 | 108 | 142 | 174 | 210 | 253
30 Pa - Max noise, dB(A) |  |  | 37 | 38 | 41 | 44 | 45 | 46 | 48 | 48 | 49
50 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 110.6 | 154.9 | 210.9 | 282.3 | 317 | 383.9 | 452.8 | 545.9 | 578.3
50 Pa - s0 |  |  | -295.2 | -391 | -570.6 | -710.8 | -738.2 | -927.4 | -1213.2 | -1423.4 | -1469.5
50 Pa - h1 |  |  | 94.4 | 135.6 | 182.5 | 223.9 | 266.3 | 322.4 | 377.9 | 460 | 494.8
50 Pa - h0 |  |  | -266.4 | -367 | -520.4 | -625.4 | -689.1 | -896.7 | -1120.7 | -1350.3 | -1453.7
50 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
50 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
50 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
50 Pa - Max noise, dB(A) |  |  | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56

## DF2 EC Select
Cooling / Heating
[10 empty] | Inlet water temperature, °C | 7 | dT
[10 empty] | Outlet water temperature, °C | 12
[10 empty] | Room temperature, °C | 27
[5 empty] | Ducted Fan Coil Units DF |  |  |  |  | External static pressure, Pa | 12
[10 empty] | Room relative humidity, % | 47 | dx latent
[10 empty] | Required capacity, W | 2500
[5 empty] | Technical specifications |  |  |  |  | Tolerance + | 15%
[10 empty] | Tolerance - | 2%
[5 empty] | EC motors |  | 2 - pipes
Model |  |  | DF23-34-B-EC DF23-34-E-EC | DF23-51-B-EC DF23-51-E-EC | DF23-68-B-EC DF23-68-E-EC | DF23-85-B-EC DF23-85-E-EC | DF23-102-B-EC DF23-102-E-EC | DF23-136-B-EC DF23-136-E-EC | DF23-170-B-EC DF23-170-E-EC | DF23-204-B-EC DF23-204-E-EC | DF23-238-B-EC DF23-238-E-EC
Air flow | m3/h | High |  | 631 | 802 | 984 | 1155 | 1594 | 1872 | 2204 | 2621
|  | Med. |  | 470 | 586 | 722 | 847 | 1172 | 1381 | 1612 | 1925
|  | Low |  | 310 | 383 | 476 | 558 | 776 | 900 | 1066 | 1272
Total cooling capacity | W | High
|  | Med. |  | 3054 | 3958 | 4503 | 5593 | 7166 | 7794 | 9342 | 10666
|  | Low |  | 1672 | 2333 | 2972 | 3985 | 5023 | 5504 | 6593 | 7490
Sensible cooling capacity | W | High |  | 2625 | 3294.95 | 3832.25 | 4743.3 | 6613.3 | 7083.05 | 8752.8 | 9585.15
|  | Med. |  | 2339 | 3025 | 3484 | 4288 | 5463 | 5929 | 7169 | 8176
|  | Low |  | 1281 | 1783 | 2299 | 3055 | 3829 | 4186 | 5059 | 5742
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
Max. running current | A |  |  | 0.09 | 0.16 | 0.19 | 0.24 | 0.34 | 0.38 | 0.5 | 0.6
Max. sound pressure level | dB(A) |  |  | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
Water flow rate | l/h |  |  | 589.3637 | 741.4703 | 851.8573 | 1063.9983 | 1491.9347 | 1601.4187 | 1961.4961 | 2150.2837
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 26.84 | 26.63 | 28 | 36.72 | 53.3 | 53.03 | 51.25 | 49.33 | 64.05
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 2 - pipes / 3 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 11.4 | 12.5 | 15.5 | 16.5 | 17.9 | 23.9 | 25.7 | 30.7 | 31.6
Gross Weight | kg |  | 12.6 | 13.8 | 17 | 18.2 | 19.7 | 26.2 | 28.1 | 33.7 | 34.6
ESP data table for DF2 EC Select - used by the formulas above, do not edit
12 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 121.1 | 170.2 | 223.2 | 287.3 | 348.3 | 463.8 | 528.3 | 653.5 | 689.9
12 Pa - s0 |  |  | -258.6 | -337.9 | -435.3 | -597.1 | -685.7 | -906.2 | -964.6 | -1265.6 | -1284
12 Pa - h1 |  |  | 107 | 153.1 | 206.1 | 232.5 | 298.2 | 401.3 | 449.4 | 548.7 | 599.9
12 Pa - h0 |  |  | -242.3 | -345.9 | -449.2 | -551.7 | -669.6 | -858.7 | -941.5 | -1248.7 | -1329
12 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
12 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
12 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
12 Pa - Max noise, dB(A) |  |  | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
30 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 121.1 | 170.2 | 223.2 | 287.3 | 348.3 | 463.8 | 528.3 | 653.5 | 689.9
30 Pa - s0 |  |  | -258.6 | -337.9 | -435.3 | -597.1 | -685.7 | -906.2 | -964.6 | -1265.6 | -1284
30 Pa - h1 |  |  | 107 | 153.1 | 206.1 | 232.5 | 298.2 | 401.3 | 449.4 | 548.7 | 599.9
30 Pa - h0 |  |  | -242.3 | -345.9 | -449.2 | -551.7 | -669.6 | -858.7 | -941.5 | -1248.7 | -1329
30 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
30 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
30 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
30 Pa - Max noise, dB(A) |  |  | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
50 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 121.1 | 170.2 | 223.2 | 287.3 | 348.3 | 463.8 | 528.3 | 653.5 | 689.9
50 Pa - s0 |  |  | -258.6 | -337.9 | -435.3 | -597.1 | -685.7 | -906.2 | -964.6 | -1265.6 | -1284
50 Pa - h1 |  |  | 107 | 153.1 | 206.1 | 232.5 | 298.2 | 401.3 | 449.4 | 548.7 | 599.9
50 Pa - h0 |  |  | -242.3 | -345.9 | -449.2 | -551.7 | -669.6 | -858.7 | -941.5 | -1248.7 | -1329
50 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
50 Pa - Med. heating |  |  | 0.869 | 0.87 | 0.838 | 0.895 | 0.845 | 0.857 | 0.87 | 0.873 | 0.865
50 Pa - Low heating |  |  | 0.72 | 0.741 | 0.74 | 0.74 | 0.72 | 0.72 | 0.72 | 0.73 | 0.71
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
50 Pa - Max noise, dB(A) |  |  | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54

## DF4 EC Select
Cooling / Heating
[10 empty] | Inlet water temperature, °C | 7 | dT
[10 empty] | Outlet water temperature, °C | 12
[10 empty] | Room temperature, °C | 27
[5 empty] | Ducted Fan Coil Units DF |  |  |  |  | External static pressure, Pa | 12
[10 empty] | Room relative humidity, % | 47 | dx latent
[10 empty] | Required capacity, W | 2500
[5 empty] | Technical specifications |  |  |  |  | Tolerance + | 15%
[10 empty] | Tolerance - | 2%
[5 empty] | EC motors |  | 4 - pipes / 3+1 rows
Model |  |  | DF431-34-B-EC DF431-34-E-EC | DF431-51-B-EC DF431-51-E-EC | DF431-68-B-EC DF431-68-E-EC | DF431-85-B-EC DF431-85-E-EC | DF431-102-B-EC DF431-102-E-EC | DF431-136-B-EC DF431-136-E-EC | DF431-170-B-EC DF431-170-E-EC | DF431-204-B-EC DF431-204-E-EC | DF431-238-B-EC DF431-238-E-EC
Air flow | m3/h | High |  | 631 | 802 | 984 | 1155 | 1594 | 1872 | 2204 | 2621
|  | Med. |  | 470 | 586 | 722 | 847 | 1172 | 1381 | 1612 | 1925
|  | Low |  | 310 | 383 | 476 | 558 | 776 | 900 | 1066 | 1272
Total cooling capacity | W | High
|  | Med. |  | 789 | 979 | 1177 | 1446 | 1896 | 2062 | 2531 | 2887
|  | Low |  | 518 | 638 | 869 | 1013 | 1314 | 1452 | 1772 | 2013
Sensible cooling capacity | W | High |  | 896.4 | 1125.25 | 1285.2 | 1675.05 | 2308.85 | 2508.35 | 3097.65 | 3333.35
|  | Med. |  | 789 | 979 | 1177 | 1446 | 1896 | 2062 | 2531 | 2887
|  | Low |  | 518 | 638 | 869 | 1013 | 1314 | 1452 | 1772 | 2013
Heating capacity | W | High
Med.
Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
Max. running current | A |  |  | 0.09 | 0.16 | 0.19 | 0.24 | 0.34 | 0.38 | 0.5 | 0.6
Max. sound pressure level | dB(A) |  |  | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
Water flow rate | l/h | Cooling |  | 154 | 194 | 221 | 288 | 397 | 431 | 533 | 573
Heating | bar: 39; 43; 46; 50
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 11.07 | 26.44 | 37.29 | 60.75 | 53.78 | 34.94 | 39.1 | 49.68 | 62.04
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 3+1 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
[5 empty] | EC motors |  | 4 - pipes / 2+2 rows
Model |  |  | DF422-34-B-EC DF422-34-E-EC | DF422-51-B-EC DF422-51-E-EC | DF422-68-B-EC DF422-68-E-EC | DF422-85-B-EC DF422-85-E-EC | DF422-102-B-EC DF422-102-E-EC | DF422-136-B-EC DF422-136-E-EC | DF422-170-B-EC DF422-170-E-EC | DF422-204-B-EC DF422-204-E-EC | DF422-238-B-EC DF422-238-E-EC
Air flow | m3/h | High |  | 631 | 802 | 984 | 1155 | 1594 | 1872 | 2204 | 2621
|  | Med. |  | 470 | 586 | 722 | 847 | 1172 | 1381 | 1612 | 1925
|  | Low |  | 310 | 383 | 476 | 558 | 776 | 900 | 1066 | 1272
Total cooling capacity | W | High | bar: 39; 43; 46; 50
|  | Med. |  | 743 | 962 | 1142 | 1298 | 1416 | 1689 | 2010 | 2316
|  | Low |  | 529 | 669 | 805 | 951 | 1095 | 1199 | 1452 | 1659
Sensible cooling capacity | W | High |  | 791.25 | 1049.2 | 1231.6 | 1451.55 | 1794.95 | 2008.15 | 2436.95 | 2680.1
|  | Med. |  | 743 | 962 | 1142 | 1298 | 1416 | 1689 | 2010 | 2316
|  | Low |  | 529 | 669 | 805 | 951 | 1095 | 1199 | 1452 | 1659
Heating capacity | W | High | bar: 39; 43; 46; 50
Med. | bar: 39; 43; 46; 50
Low | bar: 39; 43; 46; 50
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  |  | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
Max. running current | A |  |  | 0.09 | 0.16 | 0.19 | 0.24 | 0.34 | 0.38 | 0.5 | 0.6
Max. sound pressure level | dB(A) |  |  | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
Water flow rate | l/h | Cooling |  | 136 | 180 | 212 | 250 | 309 | 345 | 419 | 461
Heating | bar: 39; 43; 46; 50
Water-side pressure drop | kPa | Cooling 7/12/27C | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
|  | Heating 75/65/20C | 22.29 | 25.42 | 24.69 | 36.51 | 52.26 | 41.33 | 46.87 | 43.66 | 56.18
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Forward curve centrifugal fan
Motor Type |  |  | EC fan motor with 0–10 V control
Heat exchanger type |  |  | 4 - pipes / 2+2 rows
Heat exchanger Material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | 3/4" Female
Condensate drain connection |  |  | 3/4" Male
Unit dimensions W × D × H | mm |  | 670x504x242 (B) / 670x520x230 (E) | 770x504x242 (B) / 770x520x230 (E) | 970x504x242 (B) / 970x520x230 (E) | 1070x504x242 (B) / 1070x520x230 (E) | 1170x504x242 (B) / 1170x520x230 (E) | 1370x504x242 (B) / 1370x520x230 (E) | 1470x504x242 (B) / 1470x520x230 (E) | 1770x504x242 (B) / 1770x520x230 (E) | 1870x504x242 (B) / 1870x520x230 (E)
Packed dimensions W × D × H | mm |  | 700x530x260 | 800x530x260 | 1000x530x260 | 1100x530x260 | 1200x530x260 | 1400x530x260 | 1500x530x260 | 1800x530x260 | 1900x530x260
Unit Weight | kg |  | 12.8 | 14.1 | 17 | 18 | 19.4 | 26.7 | 28.4 | 33.2 | 33.8
Gross Weight | kg |  | 14 | 15.4 | 18.5 | 19.7 | 21.2 | 29 | 30.8 | 36.2 | 36.8
ESP data table for DF4 EC Select - used by the formulas above, do not edit or move
12 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 124.1 | 177.5 | 234.5 | 300.1 | 358.8 | 481.7 | 550.8 | 670 | 708.5
12 Pa - s0 |  |  | -312.3 | -465.5 | -634.6 | -821.1 | -869.2 | -1219.4 | -1359.6 | -1555 | -1607.9
12 Pa - h1 |  |  | 58.8 | 76 | 107.9 | 133.8 | 171.8 | 192.5 | 232.1 | 270.7 | 326.6
12 Pa - h0 |  |  | -298.9 | -372.7 | -519.1 | -591.7 | -651.3 | -884.7 | -992.3 | -1082.8 | -1175.5
12 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
12 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
12 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
12 Pa - Max noise, dB(A) |  |  | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
30 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 124.1 | 177.5 | 234.5 | 300.1 | 358.8 | 481.7 | 550.8 | 670 | 708.5
30 Pa - s0 |  |  | -312.3 | -465.5 | -634.6 | -821.1 | -869.2 | -1219.4 | -1359.6 | -1555 | -1607.9
30 Pa - h1 |  |  | 58.8 | 76 | 107.9 | 133.8 | 171.8 | 192.5 | 232.1 | 270.7 | 326.6
30 Pa - h0 |  |  | -298.9 | -372.7 | -519.1 | -591.7 | -651.3 | -884.7 | -992.3 | -1082.8 | -1175.5
30 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
30 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
30 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
30 Pa - Max noise, dB(A) |  |  | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
50 Pa - w1 |  |  | 149993 | 232248 | 299987 | 154832 | 319341 | 483850 | 532235 | 716097 | 822544
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 124.1 | 177.5 | 234.5 | 300.1 | 358.8 | 481.7 | 550.8 | 670 | 708.5
50 Pa - s0 |  |  | -312.3 | -465.5 | -634.6 | -821.1 | -869.2 | -1219.4 | -1359.6 | -1555 | -1607.9
50 Pa - h1 |  |  | 58.8 | 76 | 107.9 | 133.8 | 171.8 | 192.5 | 232.1 | 270.7 | 326.6
50 Pa - h0 |  |  | -298.9 | -372.7 | -519.1 | -591.7 | -651.3 | -884.7 | -992.3 | -1082.8 | -1175.5
50 Pa - Med. cooling |  |  | 0.899 | 0.904 | 0.914 | 0.916 | 0.898 | 0.91 | 0.91 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.728 | 0.744 | 0.736 | 0.737 | 0.722 | 0.736 | 0.735 | 0.728 | 0.742
50 Pa - Med. heating |  |  | 0.871 | 0.869 | 0.838 | 0.894 | 0.846 | 0.857 | 0.87 | 0.873 | 0.865
50 Pa - Low heating |  |  | 0.718 | 0.742 | 0.74 | 0.74 | 0.721 | 0.721 | 0.72 | 0.73 | 0.71
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
50 Pa - Max noise, dB(A) |  |  | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54
ESP data table for DF4 EC Select - used by the formulas above, do not edit or move
12 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
12 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 Pa - s1 |  |  | 108.9 | 153.6 | 202.6 | 282.9 | 320.1 | 387.3 | 446.7 | 535.7 | 565.2
12 Pa - s0 |  |  | -265.7 | -368.5 | -426.1 | -720.1 | -791.3 | -988.1 | -1107.1 | -1245.6 | -1240.5
12 Pa - h1 |  |  | 93.8 | 135.1 | 179.8 | 223 | 266.5 | 322.1 | 375.7 | 455.8 | 489.2
12 Pa - h0 |  |  | -243.6 | -350 | -426.4 | -591.4 | -696.8 | -885.7 | -1041.6 | -1202.1 | -1256.5
12 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
12 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
12 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
12 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
12 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
12 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
12 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
12 Pa - Max power, W |  |  | 17 | 20 | 36 | 44 | 56 | 78 | 88 | 114 | 139
12 Pa - Max noise, dB(A) |  |  | 35 | 37 | 39 | 41 | 43 | 44 | 46 | 48 | 50
30 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
30 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Pa - s1 |  |  | 108.9 | 153.6 | 202.6 | 282.9 | 320.1 | 387.3 | 446.7 | 535.7 | 565.2
30 Pa - s0 |  |  | -265.7 | -368.5 | -426.1 | -720.1 | -791.3 | -988.1 | -1107.1 | -1245.6 | -1240.5
30 Pa - h1 |  |  | 93.8 | 135.1 | 179.8 | 223 | 266.5 | 322.1 | 375.7 | 455.8 | 489.2
30 Pa - h0 |  |  | -243.6 | -350 | -426.4 | -591.4 | -696.8 | -885.7 | -1041.6 | -1202.1 | -1256.5
30 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
30 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
30 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
30 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
30 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
30 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
30 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
30 Pa - Max power, W |  |  | 26 | 34 | 42 | 51 | 63 | 91 | 101 | 140 | 166
30 Pa - Max noise, dB(A) |  |  | 38 | 40 | 42 | 44 | 45 | 46 | 48 | 50 | 52
50 Pa - w1 |  |  | 135478 | 203217 | 270956 | 145155 | 285471 | 387080 | 430626 | 575781 | 658035
50 Pa - w0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 Pa - s1 |  |  | 108.9 | 153.6 | 202.6 | 282.9 | 320.1 | 387.3 | 446.7 | 535.7 | 565.2
50 Pa - s0 |  |  | -265.7 | -368.5 | -426.1 | -720.1 | -791.3 | -988.1 | -1107.1 | -1245.6 | -1240.5
50 Pa - h1 |  |  | 93.8 | 135.1 | 179.8 | 223 | 266.5 | 322.1 | 375.7 | 455.8 | 489.2
50 Pa - h0 |  |  | -243.6 | -350 | -426.4 | -591.4 | -696.8 | -885.7 | -1041.6 | -1202.1 | -1256.5
50 Pa - Med. cooling |  |  | 0.901 | 0.905 | 0.913 | 0.916 | 0.898 | 0.85 | 0.913 | 0.901 | 0.919
50 Pa - Low cooling |  |  | 0.729 | 0.745 | 0.736 | 0.737 | 0.722 | 0.736 | 0.737 | 0.729 | 0.742
50 Pa - Med. heating |  |  | 0.87 | 0.868 | 0.839 | 0.895 | 0.846 | 0.78 | 0.791 | 0.786 | 0.795
50 Pa - Low heating |  |  | 0.72 | 0.738 | 0.74 | 0.739 | 0.72 | 0.736 | 0.734 | 0.728 | 0.742
50 Pa - Air flow High, m3/h |  |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
50 Pa - Air flow Med., m3/h |  |  | 255 | 382 | 510 | 637 | 765 | 1122 | 1402 | 1683 | 1927
50 Pa - Air flow Low, m3/h |  |  | 170 | 255 | 340 | 425 | 510 | 850 | 1062 | 1275 | 1487
50 Pa - Max power, W |  |  | 29 | 38 | 49 | 56 | 80 | 101 | 125 | 173 | 208
50 Pa - Max noise, dB(A) |  |  | 40 | 42 | 44 | 45 | 47 | 48 | 50 | 52 | 54