## HWF Select
[7 empty] | Inlet water temperature, °C | 7 | Cooling / Heating | -5
[7 empty] | Outlet water temperature, °C | 12 | dT | 17.5
[7 empty] | Room temperature, °C | 27 |  | 2450
[7 empty] | Room relative humidity, % | 47 |  | 2875
|  | High wall-mounted fan coil units HWF | [6 empty] | dx latent | 0.0014325
[7 empty] | Required capacity, W | 2500
|  |  | Technical Specifications |  |  |  | Tolerance + | 15%
[7 empty] | Tolerance - | 2%
Model |  |  | HWF43-EC | HWF51-EC | HWF68-EC | HWF85-EC | HWF102-EC | HWF120-EC
Air volume | m3/h | High | 430 | 510 | 680 | 850 | 1020 | 1200
|  | Med. | 330 | 395 | 530 | 650 | 765 | 880
|  | Low | 220 | 270 | 355 | 460 | 520 | 620
Total cooling capacity | W | High | 2669.1941 | 3130.5839 | 3686.8698 | 4422.4651 | 5984.3294 | 6721.9983
| W | Med. | 2162 | 2467 | 2949 | 3613 | 4817 | 5384
| W | Low | 1511 | 1841 | 2304 | 2609 | 3501 | 4053
Sensible cooling capacity | W | High | 2149.5 | 2522.3 | 2979 | 3571.4 | 4820.8 | 5416.05
| W | Med. | 1741 | 1988 | 2383 | 2918 | 3881 | 4338
| W | Low | 1217 | 1483 | 1862 | 2107 | 2820 | 3266
Heating capacity | W | High
| W | Med.
| W | Low
Power supply |  |  | 220~230V / 1Ph / 50 or 60Hz
Max. power input | W |  | 13 | 19 | 25 | 37 | 42 | 57
Max. running current | A |  | 0.11 | 0.17 | 0.22 | 0.32 | 0.37 | 0.5
Max. sound pressure level | dB(A) | High | 32 | 35 | 41 | 47 | 45 | 49
|  | Med. | 26 | 29 | 35 | 40 | 40 | 43
|  | Low | 18 | 22 | 25 | 30 | 31 | 34
Water flow rate | l/h |  | 459.0188 | 538.3635 | 634.0275 | 760.5271 | 1029.1194 | 1155.9756
Water-side pressure drop | kPa | Cooling 7/12/27C | 24.21 | 29.83 | 23.74 | 29.98 | 32.02 | 39.58
|  | Heating 75/65/20C | 30.72 | 36.55 | 32.08 | 39.69 | 37.64 | 47.7
Max. operating pressure | Mpa |  | 1.6
Insulation Class |  |  | E
Fan Type |  |  | Cross - flow
Motor Type |  |  | EC fan motor
Heat exchanger type |  |  | 2-row finned-tube
Heat exchanger material |  |  | Copper - Aluminum
Water connections (inlet / outlet) |  |  | ZG1/2" male tapered thread
Condensate drain connection | mm |  | d16
Controller |  |  | Infrared Remote Controller (Optional: Wired Controller)
Unit dimensions W × D × H | mm |  | 850×203×291 | 850×203×291 | 972×221×303 | 972×221×303 | 1081×248×327 | 1081×248×327
Packed dimensions W × D × H | mm |  | 927×287×365 |  | 1044×304×374 |  | 1155×342×410
Unit Weight | kg |  | 9.8 | 9.8 | 12.7 | 12.7 | 15 | 15
Gross Weight | kg |  | 11.6 | 11.6 | 14.7 | 14.7 | 17.8 | 17.8